## Front_page
Field settings table
Applicable units
EHFZ03S18DJ3V
Notes
(*1) | Only applicable for models where cooling is possible
(*2) | EHFZ03S18DJ3V

## 4P596829-1A
Field settings table | [5 empty] | Installer setting at variance with default value
Breadcrumb | Field code | Setting name |  |  | Range, step Default value | Date | Value
User settings
└─ | Preset values
| └─ | Room temperature
7.4.1.1 |  | Comfort (heating) |  | R/W | [3-07]~[3-06], step: A.3.2.4 22°C
7.4.1.2 |  | Eco (heating) |  | R/W | [3-07]~[3-06], step: A.3.2.4 18°C
7.4.1.3 |  | Comfort (cooling) |  | R/W | [3-09]~[3-08], step: A.3.2.4 24°C
7.4.1.4 |  | Eco (cooling) |  | R/W | [3-09]~[3-08], step: A.3.2.4 28°C
| └─ | LWT main
7.4.2.1 | [8-09] | Comfort (heating) |  | R/W | [9-01]~[9-00], step: 1°C 35°C
7.4.2.2 | [8-0A] | Eco (heating) |  | R/W | [9-01]~[9-00], step: 1°C 33°C
7.4.2.3 | [8-07] | Comfort (cooling) |  | R/W | [9-03]~[9-02], step: 1°C 18°C
7.4.2.4 | [8-08] | Eco (cooling) |  | R/W | [9-03]~[9-02], step: 1°C 20°C
| └─ | Tank temperature
7.4.3.1 | [6-0A] | Storage comfort |  | R/W | 30~[6-0E]°C, step: 1°C 60°C
7.4.3.2 | [6-0B] | Storage eco |  | R/W | 30~min(50, [6-0E])°C, step: 1°C 50°C
7.4.3.3 | [6-0C] | Reheat |  | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
| └─ | Quiet level
7.4.4 |  |  |  | R/W | 1: Level 1 2: Level 2 3: Level 3
└─ | Set weather dependent
| └─ | Main
|  | └────────────────── | Set weather-dependent heating
7.7.1.1 | [1-00] | Set weather-dependent heating | Low ambient temp. for LWT main zone heating WD curve. | R/W | -40~5°C, step: 1°C -10°C
7.7.1.1 | [1-01] | Set weather-dependent heating | High ambient temp. for LWT main zone heating WD curve. | R/W | 10~25°C, step: 1°C 15°C
7.7.1.1 | [1-02] | Set weather-dependent heating | Leaving water value for low ambient temp. for LWT main zone heating WD curve. | R/W | [9-01]~[9-00], step: 1°C 35°C
7.7.1.1 | [1-03] | Set weather-dependent heating | Leaving water value for high ambient temp. for LWT main zone heating WD curve. | R/W | [9-01]~min(45, [9-00])°C , step: 1°C 25°C
|  | └────────────────── | Set weather-dependent Cooling
7.7.1.2 | [1-06] | Set weather-dependent Cooling | 'Low ambient temp. for LWT main zone cooling WD curve. | R/W | 10~25°C, step: 1°C 20°C
7.7.1.2 | [1-07] | Set weather-dependent Cooling | High ambient temp. for LWT main zone cooling WD curve. | R/W | 25~43°C, step: 1°C 35°C
7.7.1.2 | [1-08] | Set weather-dependent Cooling | 'Leaving water value for low ambient temp. for LWT main zone cooling WD curve. | R/W | [9-03]~[9-02]°C, step: 1°C 22°C
7.7.1.2 | [1-09] | Set weather-dependent Cooling | 'Leaving water value for high ambient temp. for LWT main zone cooling WD curve. | R/W | [9-03]~[9-02]°C, step: 1°C 18°C
| └─ | Additional
|  | └────────────────── | Set weather-dependent heating
7.7.2.1 | [0-03] | Set weather-dependent heating | Low ambient temp. for LWT add zone heating WD curve. | R/W | -40~5°C, step: 1°C -10°C
7.7.2.1 | [0-02] | Set weather-dependent heating | High ambient temp. for LWT add zone heating WD curve. | R/W | 10~25°C, step: 1°C 15°C
7.7.2.1 | [0-01] | Set weather-dependent heating | Leaving water value for low ambient temp. for LWT add zone heating WD curve. | R/W | [9-05]~[9-06]°C, step: 1°C 50°C
7.7.2.1 | [0-00] | Set weather-dependent heating | Leaving water value for high ambient temp. for LWT add zone heating WD curve. | R/W | [9-05]~min(45,[9-06])°C, step: 1°C 35°C
|  | └────────────────── | Set weather-dependent Cooling
7.7.2.2 | [0-07] | Set weather-dependent Cooling | Low ambient temp. for LWT add zone cooling WD curve. | R/W | 10~25°C, step: 1°C 20°C
7.7.2.2 | [0-06] | Set weather-dependent Cooling | High ambient temp. for LWT add zone cooling WD curve. | R/W | 25~43°C, step: 1°C 35°C
7.7.2.2 | [0-05] | Set weather-dependent Cooling | Leaving water value for low ambient temp. for LWT add zone cooling WD curve. | R/W | [9-07]~[9-08]°C, step: 1°C 12°C
7.7.2.2 | [0-04] | Set weather-dependent Cooling | Leaving water value for high ambient temp. for LWT add zone cooling WD curve. | R/W | [9-07]~[9-08]°C, step: 1°C 8°C
Installer settings
└─ | System layout
| └─ | Standard
A.2.1.1 | [E-00] | Unit type |  | R/O | 0~5 0: LT split
A.2.1.2 | [E-01] | Compressor type |  | R/O | 0
A.2.1.3 | [E-02] | Indoor software type |  | R/W (*1) R/O (*2) | 0: Reversible (*1) 1: Heating only (*2)
A.2.1.7 | [C-07] | Unit control method |  | R/W | 0: LWT control 1: Ext RT control 2: RT control
A.2.1.9 | [F-0D] | Pump operation mode |  | R/W | 0: Continuous 1: Sample 2: Request
A.2.1.A | [E-04] | Power saving possible |  | R/O | 1: Yes
A.2.1.B |  | User interface location |  | R/W | 0: At unit 1: In room
| └─ | Options
A.2.2.1 | [E-05] | DHW operation |  | R/O | 0~1 1. Yes
A.2.2.3 | [E-07] | DHW tank type |  | R/O | 0~6 1: Integrated
A.2.2.4 | [C-05] | Thermostat Type |  | R/W | 0: - 1: 1 contact 2: 2 contacts
A.2.2.A | [D-02] | Which type of DHW pump is installed? |  | R/W | 0: No 1: Secondary rtrn 2: Disinf. Shunt
A.2.2.B | [C-08] | External sensor |  | R/W | 0: No 1: Outdoor sensor 2: Room sensor
A.2.2.G |  | LAN Adapter |  | R/W | 0: No 1: Yes
└─ | Space operation
| └─ | LWT settings
|  | └────────────────── | Main
A.3.1.1.1 |  | LWT setpoint mode |  | R/W | 0: Fixed 1: Weather dep. 2: Fixed / scheduled 3: WD / scheduled
A.3.1.1.2.1 | [9-01] | Temperature range | Minimum temp (heating) | R/W | 15~37°C, step: 1°C 25°C
A.3.1.1.2.2 | [9-00] | Temperature range | Maximum temp (heating) | R/W | 37~60°C, step: 1°C 55°C
A.3.1.1.2.3 | [9-03] | Temperature range | Minimum temp (cooling) | R/W | 5~18°C, step: 1°C 5°C
A.3.1.1.2.4 | [9-02] | Temperature range | Maximum temp (cooling) | R/W | 18~22°C, step: 1°C 22°C
A.3.1.1.5 | [8-05] | Modulated LWT |  | R/W | 0: No 1: Yes
A.3.1.1.7 | [2-0C] | Emitter type |  | R/W | 0: Underfloor heating 1: Fancoil unit 2: Radiator
|  | └────────────────── | Additional
A.3.1.2.1 |  | LWT setpoint mode |  | R/W | 0: Fixed 1: Weather dep. 2: Fixed / scheduled 3: WD / scheduled
A.3.1.2.2.1 | [9-05] | Temperature range | Minimum temp (heating) | R/W | 15~37°C, step: 1°C 25°C
A.3.1.2.2.2 | [9-06] | Temperature range | Maximum temp (heating) | R/W | 37~60°C, step: 1°C 55°C
A.3.1.2.2.3 | [9-07] | Temperature range | Minimum temp (cooling) | R/W | 5~18°C, step: 1°C 5°C
A.3.1.2.2.4 | [9-08] | Temperature range | Maximum temp (cooling) | R/W | 18~22°C, step: 1°C 22°C
|  | └────────────────── | Delta T source
A.3.1.3.1 | [1-0B] | Delta T heating |  | R/W | 3~10°C, step: 1°C 5°C
A.3.1.3.2 | [1-0D] | Delta T cooling |  | R/W | 3~10°C, step: 1°C 5°C
| └─ | Room thermostat
A.3.2.1.1 | [3-07] | Room temp. range | Minimum temp (heating) | R/W | 12~18°C, step: A.3.2.4 12°C
A.3.2.1.2 | [3-06] | Room temp. range | Maximum temp (heating) | R/W | 18~30°C, step: A.3.2.4 30°C
A.3.2.1.3 | [3-09] | Room temp. range | Minimum temp (cooling) | R/W | 15~25°C, step: A.3.2.4 15°C
A.3.2.1.4 | [3-08] | Room temp. range | Maximum temp (cooling) | R/W | 25~35°C, step: A.3.2.4 35°C
A.3.2.2 | [2-0A] | Room temp. offset |  | R/W | -5~5°C, step: 0,5°C 0°C
A.3.2.4 |  | Room temp. step |  | R/W | 0: 1°C 1: 0,5°C
| └─ | Operation range
A.3.3.1 | [4-02] | Space heating OFF temp |  | R/W | 14~35°C, step: 1°C 22°C
A.3.3.2 | [F-01] | Space Cooling ON temp |  | R/W | 10~35°C, step: 1°C 20°C
└─ | Domestic hot water (DHW)
| └─ | Type
A.4.1 | [6-0D] |  |  | R/W | 0: Reheat only 1: Reheat + sched. 2: Scheduled only
| └─ | Disinfection
A.4.4.1 | [2-01] | Disinfection |  | R/W | 0: No 1: Yes
A.4.4.2 | [2-00] | Operation day |  | R/W | 0: Each day 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday 7: Sunday
A.4.4.3 | [2-02] | Start time |  | R/W | 0~23 hour, step: 1 hour 1
A.4.4.4 | [2-03] | Temperature target |  | R/W | fixed value 60°C
A.4.4.5 | [2-04] | Duration |  | R/W | 40~60 min, step: 5 min 40 min
| └─ | Maximum setpoint
A.4.5 | [6-0E] |  |  | R/W | 40~60°C, step: 1°C 60°C
| └─ | SP mode
A.4.6 |  |  |  | R/W | 0: Fixed 1: Weather dep.
| └─ | Weather dependent curve
A.4.7 | [0-0B] | Weather-dependent curve | DHW setpoint for high ambient temp. for DHW WD curve. | R/W | 35~[6-0E]°C, step: 1°C 55°C
A.4.7 | [0-0C] | Weather-dependent curve | DHW setpoint for low ambient temp. for DHW WD curve. | R/W | 45~[6-0E]°C, step: 1°C 60°C
A.4.7 | [0-0D] | Weather-dependent curve | High ambient temp. for DHW WD curve. | R/W | 10~25°C, step: 1°C 15°C
A.4.7 | [0-0E] | Weather-dependent curve | Low ambient temp. for DHW WD curve. | R/W | -40~5°C, step: 1°C -10°C
└─ | Heat sources
| └─ | Backup heater
A.5.1.4 | [5-01] | Equilibrium temp. |  | R/W | -15~35°C, step: 1°C 0°C
A.5.1.5 | [8-0E] | BUH only ambient temp. |  | R/W | -15~-7°C, step: 1°C -7°C
└─ | System operation
| └─ | Auto restart
A.6.1 | [3-00] |  |  | R/W | 0: No 1: Yes
| └─ | Pwr consumpt. Control
A.6.3.1 | [4-08] | Mode |  | R/W | 0: No limitation 1: Continuous 2: Digital inputs
A.6.3.2 | [4-09] | Type |  | R/W | 0: Current 1: Power
A.6.3.3 | [5-05] | Amp. value |  | R/W | 0~50 A, step: 1 A 50 A
A.6.3.4 | [5-09] | kW value |  | R/W | 0~20 kW, step: 0,5 kW 20 kW
| └─ | Averaging time
A.6.4 | [1-0A] |  |  | R/W | 0: No averaging 1: 12 hours 2: 24 hours 3: 48 hours 4: 72 hours
| └─ | Ext amb. sensor offset
A.6.5 | [2-0B] |  |  | R/W | -5~5°C, step: 0,5°C 0°C
| └─ | Emergency
A.6.C |  |  |  | R/W | 0: Manual 1: Automatic
| └─ | Disable protective Function
A.6.D |  | Disable protections |  | R/W | 0: No 1: Yes
└─ | Overview settings
A.8 | [0-00] | Leaving water value for high ambient temp. for LWT add zone heating WD curve. |  | R/W | [9-05]~min(45,[9-06])°C, step: 1°C 35°C
A.8 | [0-01] | Leaving water value for low ambient temp. for LWT add zone heating WD curve. |  | R/W | [9-05]~[9-06]°C, step: 1°C 50°C
A.8 | [0-02] | High ambient temp. for LWT add zone heating WD curve. |  | R/W | 10~25°C, step: 1°C 15°C
A.8 | [0-03] | Low ambient temp. for LWT add zone heating WD curve. |  | R/W | -40~5°C, step: 1°C -10°C
A.8 | [0-04] | Leaving water value for high ambient temp. for LWT add zone cooling WD curve. |  | R/W | [9-07]~[9-08]°C, step: 1°C 8°C
A.8 | [0-05] | Leaving water value for low ambient temp. for LWT add zone cooling WD curve. |  | R/W | [9-07]~[9-08]°C, step: 1°C 12°C
A.8 | [0-06] | High ambient temp. for LWT add zone cooling WD curve. |  | R/W | 25~43°C, step: 1°C 35°C
A.8 | [0-07] | Low ambient temp. for LWT add zone cooling WD curve. |  | R/W | 10~25°C, step: 1°C 20°C
A.8 | [0-0B] | Leaving water value for high ambient temp. for DHW WD curve. |  | R/W | 35~[6-0E]°C, step: 1°C 55°C
A.8 | [0-0C] | Leaving water value for low ambient temp. for DHW WD curve. |  | R/W | 45~[6-0E]°C, step: 1°C 60°C
A.8 | [0-0D] | High ambient temp. for DHW WD curve. |  | R/W | 10~25°C, step: 1°C 15°C
A.8 | [0-0E] | Low ambient temp. for DHW WD curve. |  | R/W | -40~5°C, step: 1°C -10°C
A.8 | [1-00] | Low ambient temp. for LWT main zone heating WD curve. |  | R/W | -40~5°C, step: 1°C -10°C
A.8 | [1-01] | High ambient temp. for LWT main zone heating WD curve. |  | R/W | 10~25°C, step: 1°C 15°C
A.8 | [1-02] | Leaving water value for low ambient temp. for LWT main zone heating WD curve. |  | R/W | [9-01]~[9-00], step: 1°C 35°C
A.8 | [1-03] | Leaving water value for high ambient temp. for LWT main zone heating WD curve. |  | R/W | [9-01]~min(45, [9-00])°C , step: 1°C 25°C
A.8 | [1-04] | Weather dependent cooling of the main leaving water temperature zone. |  | R/W | 0: Disabled 1: Enabled
A.8 | [1-05] | Weather dependent cooling of the additional leaving water temperature zone |  | R/W | 0: Disabled 1: Enabled
A.8 | [1-06] | Low ambient temp. for LWT main zone cooling WD curve. |  | R/W | 10~25°C, step: 1°C 20°C
A.8 | [1-07] | High ambient temp. for LWT main zone cooling WD curve. |  | R/W | 25~43°C, step: 1°C 35°C
A.8 | [1-08] | Leaving water value for low ambient temp. for LWT main zone cooling WD curve. |  | R/W | [9-03]~[9-02]°C, step: 1°C 22°C
A.8 | [1-09] | Leaving water value for high ambient temp. for LWT main zone cooling WD curve. |  | R/W | [9-03]~[9-02]°C, step: 1°C 18°C
A.8 | [1-0A] | What is the averaging time for the outdoor temp? |  | R/W | 0: No averaging 1: 12 hours 2: 24 hours 3: 48 hours 4: 72 hours
A.8 | [1-0B] | What is target delta T in heating? |  | R/W | 3~66°C, step: 1°C 5°C
A.8 | [1-0C] | What is the desired delta T in heating for the additional zone? |  | R/W | 3~10°C, step: 1°C 5°C
A.8 | [1-0D] | What is the desired delta T in cooling for the main zone? |  | R/W | 3~10°C, step: 1°C 5°C
A.8 | [1-0E] | What is the desired delta T in cooling for the additional zone? |  | R/W | 3~10°C, step: 1°C 5°C
A.8 | [2-00] | When should the disinfection function be executed? |  | R/W | 0: Each day 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday 7: Sunday
A.8 | [2-01] | Should the disinfection function be executed? |  | R/W | 0: No 1: Yes
A.8 | [2-02] | When should the disinfection function start? |  | R/W | 0~23 hour, step: 1 hour 1
A.8 | [2-03] | What is the disinfection target temperature? |  | R/W | 60°C
A.8 | [2-04] | How long must the tank temperature be maintained? |  | R/W | 40~60 min, step: 5 min 40 min
A.8 | [2-05] | Room antifrost temperature |  | R/W | 4~16°C, step: 1°C 12°C
A.8 | [2-06] | Room frost protection |  | R/W | 0: Disabled 1: Enabled
A.8 | [2-09] | Adjust the offset on the measured room temperature |  | R/W | -5~5°C, step: 0,5°C 0°C
A.8 | [2-0A] | Adjust the offset on the measured room temperature |  | R/W | -5~5°C, step: 0,5°C 0°C
A.8 | [2-0B] | What is the required offset on the measured outdoor temp.? |  | R/W | -5~5°C, step: 0,5°C 0°C
A.8 | [2-0C] | What emitter type is connected to the main LWT zone |  | R/W | 0: Underfloor heating 1: Fancoil unit 2: Radiator
A.8 | [2-0D] | What emitter type is connected to the additional LWT zone? |  | R/W | 0: Underfloor heating 1: Fancoil unit 2: Radiator
A.8 | [3-00] | Is auto restart of the unit allowed? |  | R/W | 0: No 1: Yes
A.8 | [3-01] | -- |  |  | 0
A.8 | [3-02] | -- |  |  | 1
A.8 | [3-03] | -- |  |  | 4
A.8 | [3-04] | -- |  |  | 2
A.8 | [3-05] | -- |  |  | 1
A.8 | [3-06] | What is the maximum desired room temperature in heating? |  | R/W | 18~30°C, step: 0,5°C 30°C
A.8 | [3-07] | What is the mimimum desired room temperature in heating? |  | R/W | 12~18°C, step: 0,5°C 12°C
A.8 | [3-08] | What is the maximum desired room temperature in cooling? |  | R/W | 25~35°C, step: 0,5°C 35°C
A.8 | [3-09] | What is the minimum desired room temperature in cooling? |  | R/W | 15~25°C, step: 0,5°C 15°C
A.8 | [4-00] | What is the BUH operation mode? |  | R/W | 0: Disabled 1: Enabled 2: Only DHW
A.8 | [4-01] | Which electric heater has priority? |  | R/W | 0: None 1: - 2: BUH
A.8 | [4-02] | Below which outdoor temperature is heating allowed? |  | R/W | 14~35°C, step: 1°C 22°C
A.8 | [4-03] | -- |  |  | 3
A.8 | [4-04] | Is the pump allowed during pipe freeze prevention? |  | R/O | 0: intermittent pump operation 1: Continuous pump operation 2: OFF
A.8 | [4-05] | -- |  |  | 0
A.8 | [4-06] | Emergency |  | R/W | 0: Manual 1: Automatic
A.8 | [4-08] | Which power limitation mode is required on the system? |  | R/W | 0: No limitation 1: Continuous 2: Digital inputs
A.8 | [4-09] | Which power limitation type is required? |  | R/W | 0: Current 1: Power
A.8 | [4-0A] | -- |  |  | 0
A.8 | [4-0B] | Automatic cooling/heating changeover hysteresis. |  | R/W | 1~10°C, step: 0,5°C 1°C
A.8 | [4-0D] | Automatic cooling/heating changeover offset. |  | R/W | 1~10°C, step: 0,5°C 3°C
A.8 | [5-00] | Is backup heater operation allowed above equilibrium temperature during space heating operation? |  | R/W | 0: Allowed 1: Not allowed
A.8 | [5-01] | What is the equilibrium temperature for the building? |  | R/W | -15~35°C, step: 1°C 0°C
A.8 | [5-02] | Space heating priority. |  | R/W | 0: Disabled 1: Enabled
A.8 | [5-03] | Space heating priority temperature. |  | R/W | -15~35°C, step: 1°C 0°C
A.8 | [5-04] | Set point correction for domestic hot water temperature. |  | R/W | 0~20°C, step: 1°C 10°C
A.8 | [5-05] | What is the requested limit for DI1? |  | R/W | 0~50 A, step: 1 A 50 A
A.8 | [5-06] | What is the requested limit for DI2? |  | R/W | 0~50 A, step: 1 A 50 A
A.8 | [5-07] | What is the requested limit for DI3? |  | R/W | 0~50 A, step: 1 A 50 A
A.8 | [5-08] | What is the requested limit for DI4? |  | R/W | 0~50 A, step: 1 A 50 A
A.8 | [5-09] | What is the requested limit for DI1? |  | R/W | 0~20 kW, step: 0,5 kW 20 kW
A.8 | [5-0A] | What is the requested limit for DI2? |  | R/W | 0~20 kW, step: 0,5 kW 20 kW
A.8 | [5-0B] | What is the requested limit for DI3? |  | R/W | 0~20 kW, step: 0,5 kW 20 kW
A.8 | [5-0C] | What is the requested limit for DI4? |  | R/W | 0~20 kW, step: 0,5 kW 20 kW
A.8 | [5-0D] | -- |  |  | 0
A.8 | [5-0E] | -- |  |  | 1
A.8 | [6-00] | The temperature difference determining the heat pump ON temperature. |  | R/W | 2~40°C, step: 1°C 25°C
A.8 | [6-01] | The temperature difference determining the heat pump OFF temperature. |  | R/W | 0~10°C, step: 1°C 2°C
A.8 | [6-02] | -- |  |  | 0
A.8 | [6-03] | -- |  |  | 0
A.8 | [6-04] | -- |  |  | 0
A.8 | [6-05] | -- |  |  | 0
A.8 | [6-06] | -- |  |  | 0
A.8 | [6-07] | -- |  |  | 0
A.8 | [6-08] | What is the hysteresis to be used in reheat mode? |  | R/W | 2~20°C, step: 1°C 10°C
A.8 | [6-09] | -- |  |  | 0
A.8 | [6-0A] | What is the desired comfort storage temperature? |  | R/W | 30~[6-0E]°C, step: 1°C 60°C
A.8 | [6-0B] | What is the desired eco storage temperature? |  | R/W | 30~min(50, [6-0E])°C, step: 1°C 50°C
A.8 | [6-0C] | What is the desired reheat temperature? |  | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
A.8 | [6-0D] | What is the desired DHW production type? |  | R/W | 0: Reheat only 1: Reheat + sched. 2: Scheduled only
A.8 | [6-0E] | What is the maximum temperature setpoint? |  | R/W | 40~60°C, step: 1°C 60°C
A.8 | [7-00] | -- |  |  | 0
A.8 | [7-01] | -- |  |  | 2
A.8 | [7-02] | How many leaving water temperature zones are there? |  | R/W | 0: 1 LWT zone 1: 2 LWT zones
A.8 | [7-03] | -- |  |  | 2.5
A.8 | [7-04] | -- |  |  | 0
A.8 | [7-05] | Boiler efficiency |  | R/W | 0: Very high 1: High 2: Medium 3: Low 4: Very low
A.8 | [8-00] | Minimum running time for domestic hot water operation. |  | R/W | 0~20 min, step 1 min 1 min
A.8 | [8-01] | Maximum running time for domestic hot water operation. |  | R/W | 5~95 min, step: 5 min 30 min
A.8 | [8-02] | Anti-recycling time. |  | R/W | 0~10 hour, step: 0,5 hour 0,5 hour
A.8 | [8-03] | -- |  |  | 50
A.8 | [8-04] | -- |  |  | 95
A.8 | [8-05] | Allow modulation of the LWT to control the room temp? |  | R/W | 0: No 1: Yes
A.8 | [8-06] | Leaving water temperature maximum modulation. |  | R/W | 0~10°C, step: 1°C 5°C
A.8 | [8-07] | What is the desired comfort main LWT in cooling? |  | R/W | [9-03]~[9-02], step: 1°C 18°C
A.8 | [8-08] | What is the desired eco main LWT in cooling? |  | R/W | [9-03]~[9-02], step: 1°C 20°C
A.8 | [8-09] | What is the desired comfort main LWT in heating? |  | R/W | [9-01]~[9-00]°C, step: 1°C 35°C
A.8 | [8-0A] | What is the desired eco main LWT in heating? |  | R/W | [9-01]~[9-00]°C, step: 1°C 33°C
A.8 | [8-0B] | -- |  |  | 13
A.8 | [8-0C] | -- |  |  | 10
A.8 | [8-0D] | -- |  |  | 16
A.8 | [8-0E] | What is the ambient temp for BUH only operation? |  | R/W | -15~25°C, step: 1°C -7°C
A.8 | [9-00] | What is the maximum desired LWT for main zone in heating? |  | R/W | 37~60°C, step: 1°C 55°C
A.8 | [9-01] | What is the mimimum desired LWT for main zone in heating? |  | R/W | 15~37°C, step: 1°C 25°C
A.8 | [9-02] | What is the maximum desired LWT for main zone in cooling? |  | R/W | 18~22°C, step: 1°C 22°C
A.8 | [9-03] | What is the mimimum desired LWT for main zone in cooling? |  | R/W | 5~18°C, step: 1°C 5°C
A.8 | [9-04] | Leaving water temperature overshoot temperature. |  | R/W | 1~4°C, step: 1°C 1°C
A.8 | [9-05] | What is the mimimum desired LWT for add. zone in heating? |  | R/W | 15~37°C, step: 1°C 25°C
A.8 | [9-06] | What is the maximum desired LWT for add. zone in heating? |  | R/W | 37~55, step: 1°C 55°C
A.8 | [9-07] | What is the mimimum desired LWT for add. zone in cooling? |  | R/W | 5~18°C, step: 1°C 5°C
A.8 | [9-08] | What is the maximum desired LWT for add. zone in cooling? |  | R/W | 18~22°C, step: 1°C 22°C
A.8 | [9-0C] | Room temperature hysteresis. |  | R/W | 1~6°C, step: 0,5°C 1 °C
A.8 | [9-0D] | Pump speed limitation |  | R/W | 0~8, step:1 0 : No limitation 1~4 : 50~80% 5~8 : 50~80% during sampling 6
A.8 | [9-0E] | Pump speed limitation additional Zone |  | R/W | 0~8, step:1 0 : No limitation 1~4 : 50~80% 5~8 : 50~80% during sampling 6
A.8 | [C-00] | -- |  |  | 0
A.8 | [C-01] | -- |  |  | 0
A.8 | [C-02] | Is an external backup heat source connected? |  | R/W | 0: No 1: Bivalent
A.8 | [C-03] | Bivalent activation temperature. |  | R/W | -25~25°C, step: 1°C 0°C
A.8 | [C-04] | Bivalent hysteresis temperature. |  | R/W | 2~10°C, step 1°C 3°C
A.8 | [C-05] | What is the thermo request contact type for the main zone? |  | R/W | 0: - 1: 1 contact 2: 2 contacts
A.8 | [C-06] | What is the thermo request contact type for the add. zone? |  | R/W | 0: - 1: 1 contact 2: 2 contacts
A.8 | [C-07] | What is the unit control method in space operation? |  | R/W | 0: LWT control 1: Ext RT control 2: RT control
A.8 | [C-08] | Which type of external sensor is installed? |  | R/W | 0: No 1: Outdoor sensor 2: Room sensor
A.8 | [C-09] | What is the required alarm output contact type? |  | R/W | 0: Normally open 1: Normally closed
A.8 | [C-0A] | -- |  |  | 0
A.8 | [C-0C] | -- |  |  | 0
A.8 | [C-0D] | -- |  |  | 0
A.8 | [C-0E] | -- |  |  | 0
A.8 | [D-00] | Which heaters are permitted if prefer. kWh rate PS is cut? |  | R/W | 0: None 1: - 2: BUH only 3: -
A.8 | [D-01] | Contact type of preferential kWh rate PS installation? |  | R/W | 0: No 1: Active open 2: Active closed 3: Safety thermostat
A.8 | [D-02] | Which type of DHW pump is installed? |  | R/W | 0: No 1: Secondary rtrn 2: Disinf. Shunt
A.8 | [D-03] | Leaving water temperature compensation around 0°C. |  | R/W | 0: No 1: increase 2°C, span 4°C 2: increase 4°C, span 4°C 3: increase 2°C, span 8°C 4: increase 4°C, span 8°C
A.8 | [D-04] | Is a demand PCB connected? |  | R/W | 0: No 1: Pwr consmp ctrl
A.8 | [D-05] | Is the pump allowed to run if prefer. kWh rate PS is cut? |  | R/W | 0: Forced off 1: As normal
A.8 | [D-07] | Is a solar kit connected? |  | R/W | 0: No 1: Yes
A.8 | [D-08] | Is an external kWh meter used for power measurement? |  | R/W | 0: No 1: 0,1 pulse/kWh 2: 1 pulse/kWh 3: 10 pulse/kWh 4: 100 pulse/kWh 5: 1000 pulse/kWh
A.8 | [D-09] | Is an external kWh meter used for power measurement? |  | R/W | 0: No 1: 0,1 pulse/kWh 2: 1 pulse/kWh 3: 10 pulse/kWh 4: 100 pulse/kWh 5: 1000 pulse/kWh
A.8 | [D-0A] | -- |  |  | 0
A.8 | [D-0B] | -- |  |  | 2
A.8 | [D-0C] | -- |  |  | 0
A.8 | [D-0D] | -- |  |  | 0
A.8 | [D-0E] | -- |  |  | 0
A.8 | [E-00] | Which type of unit is installed? |  | R/O | 0~5 0: LT split
A.8 | [E-01] | Which type of compressor is installed? |  | R/O | 0
A.8 | [E-02] | What is the indoor unit software type? |  | R/W (*1) R/O (*2) | 0: Reversible (*1) 1: Heating only (*2)
A.8 | [E-03] | -- |  | R/O | 2
A.8 | [E-04] | Is the power saving function available on the outdoor unit? |  | R/O | 0: No 1: Yes
A.8 | [E-05] | Can the system prepare domestic hot water? |  | R/O | 0~1 1: Yes
A.8 | [E-06] | Is a DHW tank installed in the system? |  | R/O | 0~1 1: Yes
A.8 | [E-07] | What kind of DHW tank is installed? |  | R/O | 0~6 1: Integrated
A.8 | [E-08] | Power saving function for outdoor unit. |  | R/O | 0~1 1: Enabled
A.8 | [E-09] | -- |  |  | 1
A.8 | [E-0A] | -- |  |  | 0
A.8 | [E-0B] | -- |  |  | 1
A.8 | [E-0C] | -- |  |  | 0
A.8 | [E-0D] | Is the system filled with glycol? |  | R/W | 0: No 1: Yes
A.8 | [E-0E] | -- |  |  | 0
A.8 | [F-00] | Pump operation allowed outside range. |  | R/W | 0: Disabled 1: Enabled
A.8 | [F-01] | Above which outdoor temperature is cooling allowed? |  | R/W | 10~35°C, step: 1°C 20°C
A.8 | [F-02] | -- |  |  | 3
A.8 | [F-03] | -- |  |  | 5
A.8 | [F-04] | -- |  |  | 0
A.8 | [F-05] | -- |  |  | 0
A.8 | [F-09] | Pump operation during flow abnormality. |  | R/W | 0: Disabled 1: Enabled
A.8 | [F-0A] | -- |  |  | 0
A.8 | [F-0B] | Close shut-off valve during thermo OFF? |  | R/W | 0: No 1: Yes
A.8 | F-0C | Close shut-off valve during cooling? |  | R/W | 0: No 1: Yes
A.8 | [F-0D] | What is the pump operation mode? |  | R/W | 0: Continuous 1: Sample 2: Request