## Front_page
Field settings table
Applicable indoor units
ELBH12E▲6V▼
ELBH12E▲9W▼
ELBX12E▲6V▼
ELBX12E▲9W▼
ELVH12S18▲6V▼
ELVH12S23E▲6V▼
ELVH12S18E▲9W▼
ELVH12S23E▲9W▼
ELVX12S18E▲6V▼
ELVX12S23E▲6V▼
ELVX12S18E▲9W▼
ELVX12S23E▲9W▼
Notes
(*1) | *6V*
(*2) | *9W*
(*3) | ELB*
(*4) | ELV*
(*5) | *X*
(*6) | *H*
▲ | = 1, 2, 3, …, 9, A, B, C, …, Z
▼ | = , , 1, 2, 3, …, 9

## 4P717809-1
Field settings table |  |  |  |  | Installer setting at variance with default value
Breadcrumb | Field code | Setting name |  | Range, step Default value | Date | Value
Room
└─ | Antifrost
1.4.1 | [2-06] | Activation | R/W | 0: No 1: Yes
1.4.2 | [2-05] | Room setpoint | R/W | 4~16°C, step: 1°C 8°C
└─ | Setpoint range
1.5.1 | [3-07] | Heating minimum | R/W | 12~18°C, step: 1°C 12°C
1.5.2 | [3-06] | Heating maximum | R/W | 18~30°C, step: 1°C 30°C
1.5.3 | [3-09] | Cooling minimum | R/W | 15~25°C, step: 1°C 15°C
1.5.4 | [3-08] | Cooling maximum | R/W | 25~35°C, step: 1°C 35°C
Room
1.6 | [2-09] | Room sensor offset | R/W | -5~5°C, step: 0,5°C 0°C
1.7 | [2-0A] | Room sensor offset | R/W | -5~5°C, step: 0,5°C 0°C
└─ | Room comfort setpoint
1.9.1 | [9-0A] | Heating comfort setpoint | R/W | [3-07]~[3-06]°C, step: 0,5°C 23°C
1.9.2 | [9-0B] | Cooling comfort setpoint | R/W | [3-09]~[3-08]°C, step: 0,5°C 23°C
Main zone
2.4 |  | Setpoint mode |  | 0: Fixed 1: WD heating, fixed cooling 2: Weather dependent
└─ | Heating WD curve
2.5 | [1-00] | Low ambient temp. for LWT main zone heating WD curve. | R/W | -40~5°C, step: 1°C -10°C
2.5 | [1-01] | High ambient temp. for LWT main zone heating WD curve. | R/W | 10~25°C, step: 1°C 15°C
2.5 | [1-02] | Leaving water value for low ambient temp. for LWT main zone heating WD curve. | R/W | [9-01]~[9-00], step: 1°C [2-0C]=0 40°C [2-0C]=1 45°C [2-0C]=2 55°C
2.5 | [1-03] | Leaving water value for high ambient temp. for LWT main zone heating WD curve. | R/W | [9-01]~min(45, [9-00])°C , step: 1°C 25°C
└─ | Cooling WD curve
2.6 | [1-06] | Low ambient temp. for LWT main zone cooling WD curve. | R/W | 10~25°C, step: 1°C 20°C
2.6 | [1-07] | High ambient temp. for LWT main zone cooling WD curve. | R/W | 25~43°C, step: 1°C 35°C
2.6 | [1-08] | Leaving water value for low ambient temp. for LWT main zone cooling WD curve. | R/W | [9-03]~[9-02]°C, step: 1°C 22°C
2.6 | [1-09] | Leaving water value for high ambient temp. for LWT main zone cooling WD curve. | R/W | [9-03]~[9-02]°C, step: 1°C [2-0C]=0: 18°C [2-0C]=1: 7°C [2-0C]=2: 18°C
Main zone
2.7 | [2-0C] | Emitter type | R/W | 0: Underfloor heating 1: Fancoil unit 2: Radiator
└─ | Setpoint range
2.8.1 | [9-01] | Heating minimum | R/W | 15~37°C, step: 1°C 25°C
2.8.2 | [9-00] | Heating maximum | R/W | 37~65, step: 1°C [2-0C]=2: 65°C [2-0C]≠2: 55°C
2.8.3 | [9-03] | Cooling minimum | R/W | 5~18°C, step: 1°C 7°C
2.8.4 | [9-02] | Cooling maximum | R/W | 18~22°C, step: 1°C 22°C
Main zone
2.9 | [C-07] | Control | R/W | 0: Leaving water 1: External room thermostat 2: Room thermostat
2.A | [C-05] | Ext Thermostat type | R/W | 0: - 1: 1 contact 2: 2 contacts
└─ | Delta T
2.B.1 | [1-0B] | Delta T heating | R/W | 3~12°C, step: 1°C [2-0C] ≠ 2 (Radiator) 5°C [2-0C] = 2 (Radiator) 10°C
2.B.2 | [1-0D] | Delta T cooling | R/W | 3~10°C, step: 1°C 5°C
└─ | Modulation
2.C.1 | [8-05] | Modulation | R/W | 0: No 1: Yes
2.C.2 | [8-06] | Max modulation | R/W | 0~10°C, step: 1°C 5°C
└─ | Shut off valve
2.D.1 | [F-0B] | During thermo | R/W | 0: No 1: Yes
2.D.2 | [F-0C] | During cooling | R/W | 0: No 1: Yes
Main zone
2.E |  | WD curve type | R/W | 0: 2-points 1: Slope-Offset
Additional zone
3.4 |  | Setpoint mode |  | 0: Fixed 1: WD heating, fixed cooling 2: Weather dependent
└─ | Heating WD curve
3.5 | [0-00] | Leaving water value for high ambient temp. for LWT add zone heating WD curve. | R/W | [9-05]~min(45,[9-06])°C, step: 1°C 25°C
3.5 | [0-01] | Leaving water value for low ambient temp. for LWT add zone heating WD curve. | R/W | [9-05]~[9-06]°C, step: 1°C [2-0C]=0 40°C [2-0C]=1 45°C [2-0C]=2 55°C
3.5 | [0-02] | High ambient temp. for LWT add zone heating WD curve. | R/W | 10~25°C, step: 1°C 15°C
3.5 | [0-03] | Low ambient temp. for LWT add zone heating WD curve. | R/W | -40~5°C, step: 1°C -10°C
└─ | Cooling WD curve
3.6 | [0-04] | Leaving water value for high ambient temp. for LWT add zone cooling WD curve. | R/W | [9-07]~[9-08]°C, step: 1°C [2-0C]=0: 18°C [2-0C]=1: 7°C [2-0C]=2: 18°C
3.6 | [0-05] | Leaving water value for low ambient temp. for LWT add zone cooling WD curve. | R/W | [9-07]~[9-08]°C, step: 1°C 22°C
3.6 | [0-06] | High ambient temp. for LWT add zone cooling WD curve. | R/W | 25~43°C, step: 1°C 35°C
3.6 | [0-07] | Low ambient temp. for LWT add zone cooling WD curve. | R/W | 10~25°C, step: 1°C 20°C
Additional zone
3.7 | [2-0D] | Emitter type | R/O | 0: Underfloor heating 1: Fancoil unit 2: Radiator
└─ | Setpoint range
3.8.1 | [9-05] | Heating minimum | R/W | 15~37°C, step: 1°C 25°C
3.8.2 | [9-06] | Heating maximum | R/W | 37~65, step: 1°C [2-0C]=2: 65°C [2-0C]≠2: 55°C
3.8.3 | [9-07] | Cooling minimum | R/W | 5~18°C, step: 1°C 7°C
3.8.4 | [9-08] | Cooling maximum | R/W | 18~22°C, step: 1°C 22°C
Additional zone
3.A | [C-06] | Ext Thermostat type | R/W | 1: 1 contact 2: 2 contacts
└─ | Delta T
3.B.1 | [1-0C] | Delta T heating | R/W | 3~12°C, step: 1°C [2-0C] ≠ 2 (Radiator) 5°C [2-0C] = 2 (Radiator) 10°C
3.B.2 | [1-0E] | Delta T cooling | R/W | 3~10°C, step: 1°C 5°C
Additional zone
3.C |  | WD curve type | R/O | 0: 2-points 1: Slope-Offset
Space heating / cooling
└─ | Operation range
4.3.1 | [4-02] | Space heating OFF temp | R/W | 14~35°C, step: 1°C 35°C
4.3.2 | [F-01] | Space cooling OFF temp | R/W | 10~35°C, step: 1°C 20°C
Space heating / cooling
4.4 | [7-02] | Number of zones | R/W | 0: Single zone 1: Dual zone
4.5 | [F-0D] | Pump operation mode | R/W | 0: Continuous 1: Sample 2: Request
4.6 | [E-02] | Unit type | R/W (*5) R/O (*6) | 0: Reversible (*5) 1: Heating only (*6)
4.7 | [9-0D] | Pump limitation | R/W | 0~8, step:1 0: No limitation 1~4: 90~60% pump speed 5~8: 90~60% pump speed during sampling 6
Space heating / cooling
4.9 | [F-00] | Pump outside range | R/W | 0: Restricted 1: Allowed
4.A | [D-03] | Increase around 0°C | R/W | 0: No 1: increase 2°C, span 4°C 2: increase 4°C, span 4°C 3: increase 2°C, span 8°C 4: increase 4°C, span 8°C
4.B | [9-04] | Overshoot | R/W | 1~4°C, step: 1°C 2°C
4.C | [2-06] | Antifrost | R/W | 0: No 1: Yes
Tank
5.2 | [6-0A] | Comfort setpoint | R/W | 30~[6-0E]°C, step: 1°C 60°C
5.3 | [6-0B] | Eco setpoint | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
5.4 | [6-0C] | Reheat setpoint | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
5.6 | [6-0D] | Heat up mode | R/W | 0: Reheat only 1: Schedule + reheat 2: Scheduled only
└─ | Disinfection
5.7.1 | [2-01] | Activation | R/W | 0: No 1: Yes
5.7.2 | [2-00] | Operation day | R/W | 0: Each day 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday 7: Sunday
5.7.3 | [2-02] | Start time | R/W | 0~23 hour, step: 1 hour 1
5.7.4 | [2-03] | Tank setpoint | R/W | 60°C
5.7.5 | [2-04] | Duration | R/W | 40~60 min, step: 5 min 40 min
Tank
5.8 | [6-0E] | Maximum | R/W | (*3) [E-07]=0 or 7: 40~ 60°C, step: 1°C 60°C (*3) [E-07]=3 or 8: 40~75°C, step: 1°C 75°C (*3) [E-07]=5: 40~80°C, step: 1°C 80°C (*4) : 40~65°C, step: 1°C 65°C
5.9 | [6-00] | Hysteresis | R/W | 2~40°C, step: 1°C 8°C
5.A | [6-08] | Hysteresis | R/W | 2~20°C, step: 1°C 10°C
5.B |  | Setpoint mode | R/W | 0: Fixed 1: Weather dependent
└─ | WD curve
5.C | [0-0B] | Leaving water value for high ambient temp. for DHW WD curve. | R/W | 35~[6-0E]°C, step: 1°C 55°C
5.C | [0-0C] | Leaving water value for low ambient temp. for DHW WD curve. | R/W | Min(45,[6-0E])~[6-0E]°C, step: 1°C 60°C
5.C | [0-0D] | High ambient temp. for DHW WD curve. | R/W | 10~25°C, step: 1°C 15°C
5.C | [0-0E] | Low ambient temp. for DHW WD curve. | R/W | -40~5°C, step: 1°C -10°C
Tank
5.D | [6-01] | Margin | R/W | 0~10°C, step: 1°C 0°C
5.E |  | WD curve type | R/O | 0: 2-points 1: Slope-Offset
User settings
└─ | Quiet
7.4.1 |  | Mode | R/W | 0: OFF 1: Manual 2: Automatic
7.4.3 |  | Level | R/W | 0: Quiet 1: More Quiet 2: Most Quiet
└─ | Electricity price
7.5.1 |  | High | R/W | 0,00~990/kWh 1/kWh
7.5.2 |  | Medium | R/W | 0,00~990/kWh 1/kWh
7.5.3 |  | Low | R/W | 0,00~990/kWh 1/kWh
User settings
7.6 |  | Gas price | R/W | 0,00~990/kWh 0,00~290/MBtu 1,0/kWh
Installer settings
└─ | Configuration wizard
| └─ | System
9.1.3.2 | [E-03] | BUH type | R/O | 3: 6V (*1) 4: 9W (*2)
9.1.3.3 | [E-05] [E-06] [E-07] | Domestic hot water | R/W | No DHW (*3) EKHWS/E, small volume (*3) Integrated (*4) EKHWS/E, big volume (*3) EKHWP/HYC (*3) 3rd party, small coil (*3) 3rd party, big coil (*3)
9.1.3.4 | [4-06] | Emergency | R/W | 0: Manual 1: Automatic 2: Auto red SH/ DHW ON 3: Auto red SH/ DHW OFF 4: Auto normal SH/ DHW OFF
9.1.3.5 | [7-02] | Number of zones | R/W | 0: Single zone 1: Dual zone
9.1.3.6 | [E-0D] | Glycol Filled system | R/O | 0: No 1: Yes
9.1.3.7 | [6-02] | Booster heater capacity (*3) | R/W | 0~10 kW, step: 0,2 kW 3 kW (*3) 0 kW (*4)
9.1.3.8 | [C-02] | Bivalent | R/W | 0: No 1: Yes
| └─ | Backup heater
9.1.4.1 | [5-0D] | Voltage | R/W (*1) R/O (*2) | 0: 230 V, 1~ (*1) 1: 230 V, 3~ (*1) 2: 400 V, 3~ (*2)
9.1.4.2 | [4-0A] | Configuration | R/W | 0: 1 1: 1/1+2 (*1) (*2) 2: 1/2 3: 1/2 + 1/1+2 in emergency
9.1.4.3 | [6-03] | Capacity step 1 | R/W | 0~10 kW, step: 0,2 kW 2 kW (*1) 3 kW (*2)
9.1.4.4 | [6-04] | Additional capacity step 2 | R/W | 0~10 kW, step: 0,2 kW 4 kW (*1) 6 kW (*2)
| └─ | Main zone
9.1.5.1 | [2-0C] | Emitter type | R/W | 0: Underfloor heating 1: Fancoil unit 2: Radiator
9.1.5.2 | [C-07] | Control | R/W | 0: Leaving water 1: External room thermostat 2: Room thermostat
9.1.5.3 |  | Setpoint mode | R/W | 0: Fixed 1: WD heating, fixed cooling 2: Weather dependent
9.1.5.4 |  | Schedule | R/W | 0: No 1: Yes
9.1.5.5 |  | WD curve type | R/W | 0: 2-points 1: Slope-Offset
9.1.6 | [1-00] | Low ambient temp. for LWT main zone heating WD curve. | R/W | -40~5°C, step: 1°C -10°C
9.1.6 | [1-01] | High ambient temp. for LWT main zone heating WD curve. | R/W | 10~25°C, step: 1°C 15°C
9.1.6 | [1-02] | Leaving water value for low ambient temp. for LWT main zone heating WD curve. | R/W | [9-01]~[9-00], step: 1°C [2-0C]=0 40°C [2-0C]=1 45°C [2-0C]=2 55°C
9.1.6 | [1-03] | Leaving water value for high ambient temp. for LWT main zone heating WD curve. | R/W | [9-01]~min(45, [9-00])°C , step: 1°C 25°C
9.1.7 | [1-06] | Low ambient temp. for LWT main zone cooling WD curve. | R/W | 10~25°C, step: 1°C 20°C
9.1.7 | [1-07] | High ambient temp. for LWT main zone cooling WD curve. | R/W | 25~43°C, step: 1°C 35°C
9.1.7 | [1-08] | Leaving water value for low ambient temp. for LWT main zone cooling WD curve. | R/W | [9-03]~[9-02]°C, step: 1°C 22°C
9.1.7 | [1-09] | Leaving water value for high ambient temp. for LWT main zone cooling WD curve. | R/W | [9-03]~[9-02]°C, step: 1°C [2-0C]=0: 18°C [2-0C]=1: 7°C [2-0C]=2: 18°C
| └─ | Additional zone
9.1.8.1 | [2-0D] | Emitter type | R/W | 0: Underfloor heating 1: Fancoil unit 2: Radiator
9.1.8.3 |  | Setpoint mode | R/W | 0: Fixed 1: WD heating, fixed cooling 2: Weather dependent
9.1.8.4 |  | Schedule | R/W | 0: No 1: Yes
9.1.9 | [0-00] | Leaving water value for high ambient temp. for LWT add zone heating WD curve. | R/W | [9-05]~min(45,[9-06])°C, step: 1°C 25°C
9.1.9 | [0-01] | Leaving water value for low ambient temp. for LWT add zone heating WD curve. | R/W | [9-05]~[9-06]°C, step: 1°C [2-0C]=0 40°C [2-0C]=1 45°C [2-0C]=2 55°C
9.1.9 | [0-02] | High ambient temp. for LWT add zone heating WD curve. | R/W | 10~25°C, step: 1°C 15°C
9.1.9 | [0-03] | Low ambient temp. for LWT add zone heating WD curve. | R/W | -40~5°C, step: 1°C -10°C
9.1.A | [0-04] | Leaving water value for high ambient temp. for LWT add zone cooling WD curve. | R/W | [9-07]~[9-08]°C, step: 1°C [2-0C]=0: 18°C [2-0C]=1: 7°C [2-0C]=2: 18°C
9.1.A | [0-05] | Leaving water value for low ambient temp. for LWT add zone cooling WD curve. | R/W | [9-07]~[9-08]°C, step: 1°C 22°C
9.1.A | [0-06] | High ambient temp. for LWT add zone cooling WD curve. | R/W | 25~43°C, step: 1°C 35°C
9.1.A | [0-07] | Low ambient temp. for LWT add zone cooling WD curve. | R/W | 10~25°C, step: 1°C 20°C
| └─ | Tank
9.1.B.1 | [6-0D] | Heat up mode | R/W | 0: Reheat only 1: Schedule + reheat 2: Scheduled only
9.1.B.2 | [6-0A] | Comfort setpoint | R/W | 30~[6-0E]°C, step: 1°C 60°C
9.1.B.3 | [6-0B] | Eco setpoint | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
9.1.B.4 | [6-0C] | Reheat setpoint | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
9.1.B.5 | [6-08] | Hysteresis | R/W | 2~20°C, step: 1°C 10°C
└─ | Domestic hot water
9.2.1 | [E-05] [E-06] [E-07] | Domestic hot water | R/W | No DHW (*3) EKHWS/E, small volume (*3) Integrated (*4) EKHWS/E, big volume (*3) EKHWP/HYC (*3) 3rd party, small coil (*3) 3rd party, big coil (*3)
9.2.2 | [D-02] | DHW pump | R/W | 0: No DHW pump 1: Instant hot water 2: Disinfection 3: Circulation 4: Circulation and disinfection
9.2.4 | [D-07] | Solar | R/W | 0: No 1: Yes (DHW) 2: Yes (DHW + SH)
└─ | Back up heater
9.3.1 | [E-03] | BUH type | R/O | 3: 6V (*1) 4: 9W (*2)
9.3.2 | [5-0D] | Voltage | R/W (*1) R/O (*2) | 0: 230 V, 1~ (*1) 1: 230 V, 3~ (*1) 2: 400 V, 3~ (*2)
9.3.3 | [4-0A] | Configuration | R/W | 0: 1 1: 1/1+2 (*1)(*2) 2: 1/2 3: 1/2 + 1/1+2 in emergency
9.3.4 | [6-03] | Capacity step 1 | R/W | 0~10 kW, step: 0,2 kW 2 kW (*1) 3 kW (*2)
9.3.5 | [6-04] | Additional capacity step 2 | R/W | 0~10 kW, step: 0,2 kW 4 kW (*1) 6 kW (*2)
9.3.6 | [5-00] | Equilibrium | R/W | 0: No 1: Yes
9.3.7 | [5-01] | Equilibrium temperature | R/W | -15~35°C, step: 1°C 0°C
9.3.8 | [4-00] | Operation | R/W | 0: Restricted 1: Allowed 2: Only DHW
└─ | Booster heater
9.4.1 | [6-02] | Capacity | R/W | 0~10 kW, step: 0,2 kW 3 kW (*3) 0 kW (*4)
9.4.3 | [8-03] | BSH eco timer | R/W | 20~95 min, step: 5 min 50 min
9.4.4 | [4-03] | Operation | R/W | 0: Restricted 1: Allowed 2: Overlap 3: Compressor off 4: Legionella only
└─ | Emergency
9.5.1 | [4-06] | Emergency | R/W | 0: Manual 1: Automatic 2: Auto red SH/ DHW ON 3: Auto red SH/ DHW OFF 4: Auto normal SH/ DHW OFF
9.5.2 | [7-06] | Compressor forced off | R/W | 0: Disabled 1: Enabled
└─ | Balancing
9.6.1 | [5-02] | Space heating priority | R/W | 0: Disabled 1: Enabled
9.6.2 | [5-03] | Priority temperature | R/W | -15~35°C, step: 1°C 0°C
9.6.3 | [5-04] | Offset BSH setpoint | R/W | 0~20°C, step: 1°C 10°C
9.6.4 | [8-02] | Anti-recycle timer | R/W | 0~10 hour, step: 0,5 hour [E-07]=1: 0,5 hour [E-07]≠1: 3 hour
9.6.5 | [8-00] | Minimum running timer | R/W | 0~20 min, step: 1 min 1 min
9.6.6 | [8-01] | Maximum running timer | R/W | 5~95 min, step: 5 min 30 min
9.6.7 | [8-04] | Additional timer | R/W | 0~95 min, step: 5 min 95 min
Installer settings
9.7 | [4-04] | Water pipe freeze prevention | R/W | 0: Continuous pump operation 1: Non continuous pump operation 2: OFF
└─ | Benefit kWh power supply
9.8.2 | [D-00] | Allow heater | R/W | 0: No 1: Only BSH 2: Only BUH 3: All
9.8.3 | [D-05] | Allow pump | R/W | 0: No 1: Yes
9.8.4 | [D-01] | Benefit kWh power supply | R/W | 0: No 1: Open 2: Closed 3: Smart Grid
9.8.6 |  | Allow electric heaters | R/W | 0: No 1: Yes
9.8.7 |  | Enable Room buffering | R/W | 0: No 1: Yes
9.8.8 |  | Limit setting kW | R/W | 0~20 kW, step: 0,5 kW 2 kW
└─ | Power consumption control
9.9.1 | [4-08] | Power consumption control | R/W | 0: No 1: Continuous 2: Inputs 3: Current Sensor
9.9.2 | [4-09] | Type | R/W | 0: Amp 1: kW
9.9.3 | [5-05] | Limit | R/W | 0~50 A, step: 1 A 50 A
9.9.4 | [5-05] | Limit 1 | R/W | 0~50 A, step: 1 A 50 A
9.9.5 | [5-06] | Limit 2 | R/W | 0~50 A, step: 1 A 50 A
9.9.6 | [5-07] | Limit 3 | R/W | 0~50 A, step: 1 A 50 A
9.9.7 | [5-08] | Limit 4 | R/W | 0~50 A, step: 1 A 50 A
9.9.8 | [5-09] | Limit | R/W | 0~20 kW, step: 0,5 kW 20 kW
9.9.9 | [5-09] | Limit 1 | R/W | 0~20 kW, step: 0,5 kW 20 kW
9.9.A | [5-0A] | Limit 2 | R/W | 0~20 kW, step: 0,5 kW 20 kW
9.9.B | [5-0B] | Limit 3 | R/W | 0~20 kW, step: 0,5 kW 20 kW
9.9.C | [5-0C] | Limit 4 | R/W | 0~20 kW, step: 0,5 kW 20 kW
9.9.D | [4-01] | Priority heater | R/W | 0: None 1: Booster Heater 2: Backup Heater
9.9.F | [7-07] | BBR16 activation* *BBR16 settings are only visible when the language of the user interface is set to Swedish | R/W | 0: No 1: Yes
└─ | Energy metering
9.A.1 | [D-08] | Electricity meter 1 | R/W | 0: No 1: 0,1 pulse/kWh 2: 1 pulse/kWh 3: 10 pulse/kWh 4: 100 pulse/kWh 5: 1000 pulse/kWh
9.A.2 | [D-09] | Electricity meter 2 | R/W | 0: No 1: 0,1 pulse/kWh 2: 1 pulse/kWh 3: 10 pulse/kWh 4: 100 pulse/kWh 5: 1000 pulse/kWh 6: 100 pulse/kWh (PV meter) 7: 1000 pulse/kWh (PV meter)
└─ | Sensors
9.B.1 | [C-08] | External sensor | R/W | 0: No 1: Outdoor 2: Room
9.B.2 | [2-0B] | Ext. amb. sensor offset | R/W | -5~5°C, step: 0,5°C 0°C
9.B.3 | [1-0A] | Averaging time | R/W | 0: No 1: 12 h 2: 24 h 3: 48 h 4: 72 h
└─ | Bivalent
9.C.1 | [C-02] | Bivalent | R/W | 0: No 1: Yes
9.C.2 | [7-05] | Boiler efficiency | R/W | 0: Very high 1: High 2: Medium 3: Low 4: Very low
9.C.3 | [C-03] | Temperature | R/W | -25~25°C, step: 1°C 0°C
9.C.4 | [C-04] | Hysteresis | R/W | 2~10°C, step: 1°C 3°C
Installer settings
9.D | [C-09] | Alarm output | R/W | 0: Abnormal 1: Normal
9.E | [3-00] | Auto restart | R/W | 0: manual 1: automatic
9.F | [E-08] | Power saving function | R/W | 0: No 1: Yes
9.G |  | Disable protections | R/W | 0: No 1: Yes
└─ | Overview field settings
9.I | [0-00] | Leaving water value for high ambient temp. for LWT add zone heating WD curve. | R/W | [9-05]~min(45,[9-06])°C, step: 1°C 25°C
9.I | [0-01] | Leaving water value for low ambient temp. for LWT add zone heating WD curve. | R/W | [9-05]~[9-06]°C, step: 1°C [2-0C]=0 40°C [2-0C]=1 45°C [2-0C]=2 55°C
9.I | [0-02] | High ambient temp. for LWT add zone heating WD curve. | R/W | 10~25°C, step: 1°C 15°C
9.I | [0-03] | Low ambient temp. for LWT add zone heating WD curve. | R/W | -40~5°C, step: 1°C -10°C
9.I | [0-04] | Leaving water value for high ambient temp. for LWT add zone cooling WD curve. | R/W | [9-07]~[9-08]°C, step: 1°C [2-0C]=0: 18°C [2-0C]=1: 7°C [2-0C]=2: 18°C
9.I | [0-05] | Leaving water value for low ambient temp. for LWT add zone cooling WD curve. | R/W | [9-07]~[9-08]°C, step: 1°C 22°C
9.I | [0-06] | High ambient temp. for LWT add zone cooling WD curve. | R/W | 25~43°C, step: 1°C 35°C
9.I | [0-07] | Low ambient temp. for LWT add zone cooling WD curve. | R/W | 10~25°C, step: 1°C 20°C
9.I | [0-0B] | Leaving water value for high ambient temp. for DHW WD curve. | R/W | 35~[6-0E]°C, step: 1°C 55°C
9.I | [0-0C] | Leaving water value for low ambient temp. for DHW WD curve. | R/W | Min(45,[6-0E])~[6-0E]°C, step: 1°C 60°C
9.I | [0-0D] | High ambient temp. for DHW WD curve. | R/W | 10~25°C, step: 1°C 15°C
9.I | [0-0E] | Low ambient temp. for DHW WD curve. | R/W | -40~5°C, step: 1°C -10°C
9.I | [1-00] | Low ambient temp. for LWT main zone heating WD curve. | R/W | -40~5°C, step: 1°C -10°C
9.I | [1-01] | High ambient temp. for LWT main zone heating WD curve. | R/W | 10~25°C, step: 1°C 15°C
9.I | [1-02] | Leaving water value for low ambient temp. for LWT main zone heating WD curve. | R/W | [9-01]~[9-00], step: 1°C [2-0C]=0 40°C [2-0C]=1 45°C [2-0C]=2 55°C
9.I | [1-03] | Leaving water value for high ambient temp. for LWT main zone heating WD curve. | R/W | [9-01]~min(45, [9-00])°C , step: 1°C 25°C
9.I | [1-04] | Weather dependent cooling of the main leaving water temperature zone. | R/W | 0: Disabled 1: Enabled
9.I | [1-05] | Weather dependent cooling of the additional leaving water temperature zone | R/W | 0: Disabled 1: Enabled
9.I | [1-06] | Low ambient temp. for LWT main zone cooling WD curve. | R/W | 10~25°C, step: 1°C 20°C
9.I | [1-07] | High ambient temp. for LWT main zone cooling WD curve. | R/W | 25~43°C, step: 1°C 35°C
9.I | [1-08] | Leaving water value for low ambient temp. for LWT main zone cooling WD curve. | R/W | [9-03]~[9-02]°C, step: 1°C 22°C
9.I | [1-09] | Leaving water value for high ambient temp. for LWT main zone cooling WD curve. | R/W | [9-03]~[9-02]°C, step: 1°C [2-0C]=0: 18°C [2-0C]=1: 7°C [2-0C]=2: 18°C
9.I | [1-0A] | What is the averaging time for the outdoor temp? | R/W | 0: No 1: 12 h 2: 24 h 3: 48 h 4: 72 h
9.I | [1-0B] | What is the desired delta T in heating for the main zone? | R/W | 3~12°C, step: 1°C [2-0C] ≠ 2 (Radiator) 5°C [2-0C] = 2 (Radiator) 10°C
9.I | [1-0C] | What is the desired delta T in heating for the additional zone? | R/W | 3~12°C, step: 1°C [2-0C] ≠ 2 (Radiator) 5°C [2-0C] = 2 (Radiator) 10°C
9.I | [1-0D] | What is the desired delta T in cooling for the main zone? | R/W | 3~10°C, step: 1°C 5°C
9.I | [1-0E] | What is the desired delta T in cooling for the additional zone? | R/W | 3~10°C, step: 1°C 5°C
9.I | [2-00] | When should the disinfection function be executed? | R/W | 0: Each day 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday 7: Sunday
9.I | [2-01] | Should the disinfection function be executed? | R/W | 0: No 1: Yes
9.I | [2-02] | When should the disinfection function start? | R/W | 0~23 hour, step: 1 hour 1
9.I | [2-03] | What is the disinfection target temperature? | R/W | 60°C
9.I | [2-04] | How long must the tank temperature be maintained? | R/W | 40~60 min, step: 5 min 40 min
9.I | [2-05] | Room antifrost temperature | R/W | 4~16°C, step: 1°C 8°C
9.I | [2-06] | Room frost protection | R/W | 0: No 1: Yes
9.I | [2-09] | Adjust the offset on the measured room temperature | R/W | -5~5°C, step: 0,5°C 0°C
9.I | [2-0A] | Adjust the offset on the measured room temperature | R/W | -5~5°C, step: 0,5°C 0°C
9.I | [2-0B] | What is the required offset on the measured outdoor temp.? | R/W | -5~5°C, step: 0,5°C 0°C
9.I | [2-0C] | What emitter type is connected to the main LWT zone? | R/W | 0: Underfloor heating 1: Fancoil unit 2: Radiator
9.I | [2-0D] | What emitter type is connected to the additional LWT zone? | R/W | 0: Underfloor heating 1: Fancoil unit 2: Radiator
9.I | [2-0E] | What is the maximum allowed current over the heatpump? | R/W | 20~50 A, step: 1 A 50 A
9.I | [3-00] | Is auto restart of the unit allowed? | R/W | 0: manual 1: automatic
9.I | [3-01] | -- |  | 0
9.I | [3-02] | -- |  | 1
9.I | [3-03] | -- |  | 4
9.I | [3-04] | -- |  | 2
9.I | [3-05] | -- |  | 1
9.I | [3-06] | What is the maximum desired room temperature in heating? | R/W | 18~30°C, step: 1°C 30°C
9.I | [3-07] | What is the mimimum desired room temperature in heating? | R/W | 12~18°C, step: 1°C 12°C
9.I | [3-08] | What is the maximum desired room temperature in cooling? | R/W | 25~35°C, step: 1°C 35°C
9.I | [3-09] | What is the minimum desired room temperature in cooling? | R/W | 15~25°C, step: 1°C 15°C
9.I | [3-0A] | -- |  | 0
9.I | [3-0B] | -- |  | 1
9.I | [3-0C] | -- |  | 1
9.I | [3-0D] | In case a bizone kit is installed, antiblockage of kit pump(s) and kit mixing valve | R/W | 0: Disabled 1: Enabled
9.I | [4-00] | What is the BUH operation mode? | R/W | 0: Restricted 1: Allowed 2: Only DHW
9.I | [4-01] | Which electric heater has priority? | R/W | 0: None 1: Booster Heater 2: Backup Heater
9.I | [4-02] | Below which outdoor temperature is heating allowed? | R/W | 14~35°C, step: 1°C 35°C
9.I | [4-03] | Operation permission of the booster heater. | R/W | 0: Restricted 1: Allowed 2: Overlap 3: Compressor off 4: Legionella only
9.I | [4-04] | Water pipe freeze prevention | R/W | 0: Continuous pump operation 1: Non continuous pump operation 2: OFF
9.I | [4-05] | -- |  | 0
9.I | [4-06] | Emergency | R/W | 0: Manual 1: Automatic 2: Auto red SH/ DHW ON 3: Auto red SH/ DHW OFF 4: Auto normal SH/ DHW OFF
9.I | [4-08] | Which power limitation mode is required on the system? | R/W | 0: No 1: Continuous 2: Inputs 3: Current Sensor
9.I | [4-09] | Which power limitation type is required? | R/W | 0: Amp 1: kW
9.I | [4-0A] | Backup heater configuration | R/W | 0: 1 1: 1/1+2 (*1)(*2) 2: 1/2 3: 1/2 + 1/1+2 in emergency
9.I | [4-0B] | Automatic cooling/heating changeover hysteresis. | R/W | 1~10°C, step: 0,5°C 1°C
9.I | [4-0D] | Automatic cooling/heating changeover offset. | R/W | 1~10°C, step: 0,5°C 3°C
9.I | [4-0E] | -- |  | 6
9.I | [5-00] | Equilibrium: Deactivate backup heater (or external backup heat source in case of a bivalent system) above the equilibrium temperature for space heating? | R/W | 0: No 1: Yes
9.I | [5-01] | What is the equilibrium temperature for the building? | R/W | -15~35°C, step: 1°C 0°C
9.I | [5-02] | Space heating priority. | R/W | 0: Disabled 1: Enabled
9.I | [5-03] | Space heating priority temperature. | R/W | -15~35°C, step: 1°C 0°C
9.I | [5-04] | Set point correction for domestic hot water temperature. | R/W | 0~20°C, step: 1°C 10°C
9.I | [5-05] | What is the requested limit for DI1? | R/W | 0~50 A, step: 1 A 50 A
9.I | [5-06] | What is the requested limit for DI2? | R/W | 0~50 A, step: 1 A 50 A
9.I | [5-07] | What is the requested limit for DI3? | R/W | 0~50 A, step: 1 A 50 A
9.I | [5-08] | What is the requested limit for DI4? | R/W | 0~50 A, step: 1 A 50 A
9.I | [5-09] | What is the requested limit for DI1? | R/W | 0~20 kW, step: 0,5 kW 20 kW
9.I | [5-0A] | What is the requested limit for DI2? | R/W | 0~20 kW, step: 0,5 kW 20 kW
9.I | [5-0B] | What is the requested limit for DI3? | R/W | 0~20 kW, step: 0,5 kW 20 kW
9.I | [5-0C] | What is the requested limit for DI4? | R/W | 0~20 kW, step: 0,5 kW 20 kW
9.I | [5-0D] | Backup heater voltage | R/W (*1) R/O (*2) | 0: 230 V, 1~ (*1) 1: 230 V, 3~ (*1) 2: 400 V, 3~ (*2)
9.I | [5-0E] | -- |  | 1
9.I | [6-00] | The temperature difference determining the heat pump ON temperature. | R/W | 2~40°C, step: 1°C 8°C
9.I | [6-01] | The temperature difference determining the heat pump OFF temperature. | R/W | 0~10°C, step: 1°C 0°C
9.I | [6-02] | What is the capacity of the booster heater? | R/W | 0~10 kW, step: 0,2 kW 3 kW (*3) 0 kW (*4)
9.I | [6-03] | What is the capacity of the backup heater step 1? | R/W | 0~10 kW, step: 0,2 kW 2 kW (*1) 3 kW (*2)
9.I | [6-04] | What is the capacity of the backup heater step 2? | R/W | 0~10 kW, step: 0,2 kW 4 kW (*1) 6 kW (*2)
9.I | [6-05] | Keep-hot hysteresis. |  | 0~40°C, step: 1°C 12
9.I | [6-07] | -- |  | 0
9.I | [6-08] | What is the hysteresis to be used in reheat mode? | R/W | 2~20°C, step: 1°C 10°C
9.I | [6-09] | -- |  | 0
9.I | [6-0A] | What is the desired comfort storage temperature? | R/W | 30~[6-0E]°C, step: 1°C 60°C
9.I | [6-0B] | What is the desired eco storage temperature? | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
9.I | [6-0C] | What is the desired reheat temperature? | R/W | 30~min(50, [6-0E])°C, step: 1°C 45°C
9.I | [6-0D] | What is the desired DHW production type? | R/W | 0: Reheat only 1: Schedule + reheat 2: Scheduled only
9.I | [6-0E] | What is the maximum temperature setpoint? | R/W | (*3) [E-07]=0 or 7: 40~ 60°C, step: 1°C 60°C (*3) [E-07]=3 or 8: 40~75°C, step: 1°C 75°C (*3) [E-07]=5: 40~80°C, step: 1°C 80°C (*4) : 40~65°C, step: 1°C 65°C
9.I | [7-00] | Domestic hot water booster heater overshoot temperature. | R/W | 0~4°C, step: 1°C 0°C
9.I | [7-01] | Domestic hot water booster heater hysteresis. | R/W | 2~40°C, step: 1°C 2°C
9.I | [7-02] | How many leaving water temperature zones are there? | R/W | 0: Single zone 1: Dual zone
9.I | [7-03] | -- |  | 2.5
9.I | [7-04] | -- |  | 0
9.I | [7-05] | Boiler efficiency | R/W | 0: Very high 1: High 2: Medium 3: Low 4: Very low
9.I | [7-06] | Compressor forced OFF | R/W | 0: Disabled 1: Enabled
9.I | [7-07] | BBR16 activation* *BBR16 settings are only visible when the language of the user interface is set to Swedish | R/W | 0: No 1: Yes
9.I | [7-08] | Activation of keep-hot-function | R/W | 0: Disabled (*3) 1: Enabled (*4)
9.I | [7-09] | What is the minimum pump speed during space and domestic hot water operation? | R/W | 20~95%, step: 5% 20%
9.I | [7-0A] | Additional zone fixed pump PWM, in case a bizone kit is installed. | R/W | 20~95%, step: 5% 95%
9.I | [7-0B] | Main zone fixed pump PWM, in case a bizone kit is installed. | R/W | 20~95%, step: 5% 95%
9.I | [7-0C] | Time needed by the mixing valve to turn from one side to the other, in case a bizone kit is installed. | R/W | 20~300 seconds, step: 5 sec 125 seconds
9.I | [8-00] | Minimum running time for domestic hot water operation. | R/W | 0~20 min, step: 1 min 1 min
9.I | [8-01] | Maximum running time for domestic hot water operation. | R/W | 5~95 min, step: 5 min 30 min
9.I | [8-02] | Anti-recycling time. | R/W | 0~10 hour, step: 0,5 hour [E-07]=1: 0,5 hour [E-07]≠1: 3 hour
9.I | [8-03] | Booster heater delay timer. | R/W | 20~95 min, step: 5 min 50 min
9.I | [8-04] | Additional running time for the maximum running time. | R/W | 0~95 min, step: 5 min 95 min
9.I | [8-05] | Allow modulation of the LWT to control the room temp? | R/W | 0: No 1: Yes
9.I | [8-06] | Leaving water temperature maximum modulation. | R/W | 0~10°C, step: 1°C 5°C
9.I | [8-07] | What is the desired comfort main LWT in cooling? | R/W | [9-03]~[9-02], step: 1°C 18°C
9.I | [8-08] | What is the desired eco main LWT in cooling? | R/W | [9-03]~[9-02], step: 1°C 20°C
9.I | [8-09] | What is the desired comfort main LWT in heating? | R/W | [9-01]~[9-00], step: 1°C 35°C
9.I | [8-0A] | What is the desired eco main LWT in heating? | R/W | [9-01]~[9-00], step: 1°C 33°C
9.I | [8-0B] | -- |  | 13
9.I | [8-0C] | -- |  | 10
9.I | [8-0D] | -- |  | 16
9.I | [9-00] | What is the maximum desired LWT for main zone in heating? | R/W | 37~65, step: 1°C [2-0C]=2: 65°C [2-0C]≠2: 55°C
9.I | [9-01] | What is the mimimum desired LWT for main zone in heating? | R/W | 15~37°C, step: 1°C 25°C
9.I | [9-02] | What is the maximum desired LWT for main zone in cooling? | R/W | 18~22°C, step: 1°C 22°C
9.I | [9-03] | What is the mimimum desired LWT for main zone in cooling? | R/W | 5~18°C, step: 1°C 7°C
9.I | [9-04] | Leaving water temperature overshoot temperature. | R/W | 1~4°C, step: 1°C 2°C
9.I | [9-05] | What is the mimimum desired LWT for add. zone in heating? | R/W | 15~37°C, step: 1°C 25°C
9.I | [9-06] | What is the maximum desired LWT for add. zone in heating? | R/W | 37~65, step: 1°C [2-0C]=2: 65°C [2-0C]≠2: 55°C
9.I | [9-07] | What is the mimimum desired LWT for add. zone in cooling? | R/W | 5~18°C, step: 1°C 7°C
9.I | [9-08] | What is the maximum desired LWT for add. zone in cooling? | R/W | 18~22°C, step: 1°C 22°C
9.I | [9-09] | What is the allowed LWT undershoot during cooling start-up? | R/W | 1~18°C, step: 1°C 18°C
9.I | [9-0A] | What is the room buffering temperature in heating? | R/W | [3-07]~[3-06]°C, step: 0,5°C 23°C
9.I | [9-0B] | What is the room buffering temperature in cooling? | R/W | [3-09]~[3-08]°C, step: 0,5°C 23°C
9.I | [9-0C] | Room temperature hysteresis. | R/W | 1~6°C, step: 0,5°C 1°C
9.I | [9-0D] | Pump speed limitation | R/W | 0~8, step:1 0: No limitation 1~4: 90~60% pump speed 5~8: 90~60% pump speed during sampling 6
9.I | [9-0E] | -- |  | 6
9.I | [C-00] | Domestic heating water priority. | R/W | 0: Solar priority 1: Heat pump priority
9.I | [C-01] | -- |  | 0
9.I | [C-02] | Is an external backup heat source connected? | R/W | 0: No 1: Yes
9.I | [C-03] | Bivalent activation temperature. | R/W | -25~25°C, step: 1°C 0°C
9.I | [C-04] | Bivalent hysteresis temperature. | R/W | 2~10°C, step: 1°C 3°C
9.I | [C-05] | What is the thermo request contact type for the main zone? | R/W | 1: 1 contact 2: 2 contacts
9.I | [C-06] | What is the thermo request contact type for the add. zone? | R/W | 0: - 1: 1 contact 2: 2 contacts
9.I | [C-07] | What is the unit control method in space operation? | R/W | 0: Leaving water 1: External room thermostat 2: Room thermostat
9.I | [C-08] | Which type of external sensor is installed? | R/W | 0: No 1: Outdoor 2: Room
9.I | [C-09] | What is the required alarm output contact type? | R/W | 0: Abnormal 1: Normal
9.I | [C-0A] | -- |  | 0
9.I | [C-0B] | -- |  | 0
9.I | [C-0C] | -- |  | 0
9.I | [C-0D] | -- |  | 0
9.I | [C-0E] | -- |  | 0
9.I | [D-00] | Which heaters are permitted if prefer. kWh rate PS is cut? | R/W | 0: No 1: Only BSH 2: Only BUH 3: All
9.I | [D-01] | Contact type of preferential kWh rate PS installation? | R/W | 0: No 1: Open 2: Closed 3: Smart Grid
9.I | [D-02] | Which type of DHW pump is installed? | R/W | 0: No DHW pump 1: Instant hot water 2: Disinfection 3: Circulation 4: Circulation and disinfection
9.I | [D-03] | Leaving water temperature compensation around 0°C. | R/W | 0: No 1: increase 2°C, span 4°C 2: increase 4°C, span 4°C 3: increase 2°C, span 8°C 4: increase 4°C, span 8°C
9.I | [D-04] | Is a demand PCB connected? | R/W | 0: No 1: Pwr consmp ctrl
9.I | [D-05] | Is the pump allowed to run if prefer. kWh rate PS is cut? | R/W | 0: No 1: Yes
9.I | [D-07] | Is a solar kit connected? | R/W | 0: No 1: Yes (DHW) 2: Yes (DHW + SH)
9.I | [D-08] | Is an external kWh meter used for power measurement? | R/W | 0: No 1: 0,1 pulse/kWh 2: 1 pulse/kWh 3: 10 pulse/kWh 4: 100 pulse/kWh 5: 1000 pulse/kWh
9.I | [D-09] | Is an external kWh meter used for power measurement, kWh meter used for smart grid or a gas meter for hybrid unit? | R/W | 0: No 1: 0,1 pulse/kWh 2: 1 pulse/kWh 3: 10 pulse/kWh 4: 100 pulse/kWh 5: 1000 pulse/kWh 6: 100 pulse/kWh (PV meter) 7: 1000 pulse/kWh (PV meter) 8: 1 pulse/m³ (gas meter) 9: 10 pulses/m³ (gas meter) 10: 100 pulses/m³ (gas meter)
9.I | [D-0A] | -- |  | 0
9.I | [D-0B] | -- |  | 2
9.I | [D-0C] | -- |  | 0
9.I | [D-0D] | -- |  | 0
9.I | [D-0E] | -- |  | 0
9.I | [E-00] | Which type of unit is installed? | R/O | 0~5 0: LT split
9.I | [E-01] | Which type of compressor is installed? | R/O | 1
9.I | [E-02] | What is the indoor unit software type? | R/W (*5) R/O (*6) | 0: Reversible (*5) 1: Heating only (*6)
9.I | [E-03] | What is the number of backup heater steps? | R/O | 3: 6V (*1) 4: 9W (*2)
9.I | [E-04] | Is the power saving function available on the outdoor unit? | R/O | 0: No 1: Yes
9.I | [E-05] | Can the system prepare domestic hot water? | R/W | 0: No (*3) 1: Yes (*4)
9.I | [E-06] | -- |  | 1
9.I | [E-07] | What kind of DHW tank is installed? | R/W | 0~8 0: EKHWS/E, small volume (*3) 1: Integrated (*4) 3: EKHWS/E, big volume (*3) 5: EKHWP/HYC (*3) 7: Third party tank, small coil (*3) 8: Third party tank, large coil (*3)
9.I | [E-08] | Power saving function for outdoor unit. | R/W | 0: No 1: Yes
9.I | [E-09] | -- |  | 1
9.I | [E-0B] | Is a bizone kit installed? | R/W | 0: Not installed 1: - 2: Bizone kit installed
9.I | [E-0C] | What bizone system type is installed? | R/W | 0: Without hydraulic separator / no direct pump 1: With hydraulic separator / no direct pump 2: With hydraulic separator / with direct pump
9.I | [E-0D] | Is the system filled with glycol ? | R/O | 0: No 1: Yes
9.I | [E-0E] | -- |  | 0
9.I | [F-00] | Pump operation allowed outside range. | R/W | 0: Restricted 1: Allowed
9.I | [F-01] | Above which outdoor temperature is cooling allowed? | R/W | 10~35°C, step: 1°C 20°C
9.I | [F-02] | -- |  | 3
9.I | [F-03] | -- |  | 5
9.I | [F-04] | -- |  | 0
9.I | [F-05] | -- |  | 0
9.I | [F-09] | Pump operation during flow abnormality. | R/W | 0: Disabled 1: Enabled
9.I | [F-0A] | -- |  | 0
9.I | [F-0B] | Close shut-off valve during thermo OFF? | R/W | 0: No 1: Yes
9.I | [F-0C] | Close shut-off valve during cooling? | R/W | 0: No 1: Yes
9.I | [F-0D] | What is the pump operation mode? | R/W | 0: Continuous 1: Sample 2: Request
Bizone kit settings
9.P.1 | [E-0B] | Bi-zone kit installed | R/W | 0: Not installed 1: - 2: Bizone kit installed
9.P.2 | [E-0C] | Bi-zone system type | R/W | 0: Without hydraulic separator / no direct pump 1: With hydraulic separator / no direct pump 2: With hydraulic separator / with direct pump
9.P.3 | [7-0A] | Add zone pump fixed PWM | R/W | 20~95%, step: 5% 95%
9.P.4 | [7-0B] | Main zone pump fixed PWM | R/W | 20~95%, step: 5% 95%
9.P.5 | [7-0C] | Mixing valve turning time | R/W | 20~300 sec, step: 5 sec 125 sec