{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":40,"n_cols":7,"rows_kept":40,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","DucoBox Energy Comfort"]
[]
[]
[]
[]
["","","","","","DucoBox Energy Comfort 325","DucoBox Energy Comfort D400"]
["Artikelnummer","","","","","00004485","00004707"]
["Opgenomen vermogen","Warmtewisselingsmode","Nom.","Ultrahoog","kW","0.131 (1)"]
["","Bypass-mode","Nom.","Opgenomen vermogen-=-Bypass-mode-=-Nom.-=-Ultrahoog-=-kW","kW","0.131 (1)"]
["Behuizing","Materiaal","","","","Gecoat plaatstaal + EPP","Gecoat plaatstaal + EPP"]
["Afmetingen","Unit","","Hoogte","mm","705","800"]
["","","","Breedte","mm","700","756"]
["","","","Diepte","mm","525","583"]
["Gewicht","Unit","","","kg","21","47"]
["Ventilator-","Luchthoeveelheid - 50Hz","Warmtewisselingsmode","Ultrahoog","m³/u","325","400"]
["","","Bypass-mode","Ultrahoog","m³/u","325","400"]
["Ventilator","Externe statische druk - 50Hz","","Ultrahoog","Pa","100"]
["Werkingsbereik","Rondom unit","","","°CDB","-5°C~40°CDB, 90% RH of lager"]
["Geluidsdrukniveau op 1 m - 50Hz","Warmtewisselingsmode","","Ultrahoog","dBA","63"]
["","Bypass-mode","","Ultrahoog","dBA","63"]
["Warmtewisselingssysteem","","","","","Totale warmtewisselaar met lucht-luchtventilatie (voelbare + latente warmte) van het dwarsstroomtype","Totale warmtewisselaar met lucht-luchtventilatie (voelbare + latente warmte) van het dwarsstroomtype"]
["Warmtewisselingselement","","","","","PET/Polystyreen","v1: PP - v2: PET/Alu"]
["Aansluiting kanaaldiameter","mm","","","","Interne diameter Ø160","180"]
["Bedrijfsmode","","","","","Warmtewisselingsmodus, Bypass-Modus, Vorstbeschermingsmodus","Warmtewisselingsmodus, Bypass-Modus, Vorstbeschermingsmodus"]
["SEC-Klasse","","","","","A+","Zie opmerking 2"]
["Maximaal debiet bij een externe statische druk van 100 Pa","Debiet","","","m³/u","325","400"]
["Geluidsvermogenniveau (Lwa)","dB","","","","55","55"]
["Jaarlijks elektriciteitsverbruik","kWu/a","","","","117.3","231.7 (1)"]
["Jaarlijkse besparing op verwarming","Gematigd klimaat","","","kWu/a","4714","4515 (1)"]
["","Koud klimaat","","","kWu/a","9222","8833 (1)"]
["","Warm klimaat","","","kWu/a","2132","2042 (1)"]
["Voeding","Fase","","","","Een-fase geaard","3-core power cable with earthed plug"]
["Spanningsvorm","Frequentie","","","Hz","50","50"]
["","Spanning","","","V","230","230"]
["Opmerkingen","","","","","(1) - Bij max debiet","(1) - Manuele regeling (geen DCV)"]
["","","","","","(2) - Bij 250 m3/h","(2) - Met 2 sensoren (regelfactor 0,65): A+; Overige: A"]
["","","","","","(3) - Bij 100 m3/h","(3) - Dynamische luchtstroomfilter toevoerlucht (520 x 190 x 15 mm) Standaard: ISO 16890 Grof 65% (= G4) Optioneel: ISO 16890 ePM1 55% (=F7) Dynamische luchtstroomfilter afvoerlucht (520 x 190 x 15 mm) Standaard: ISO 16890 Grof 65% (= G4)"]
["","","","","","(4) - Bij 325 m3/h"]
["","","","","","(5) - Bij 332 m3/h"]
["","","","","","(6) - Bij 401 m3/h"]