{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":6,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWC-DF"]
[]
[]
[]
[]
["","","","","","FWC07DAFN5V3-- (Archived)"]
["Koelvermogen (standaardomstandigheden)","Voelbaar vermogen 4-pijps","","Laag","kW","3.26"]
["","","","Hoog","kW","5.58"]
["","Totaal vermogen 4-pijps","","Laag","kW","4.35"]
["","","","Hoog","kW","7.15"]
["Verwarmingsvermogen (standaardomstandigheden)","Vermogen 4-pijps","","Laag","kW","5.34"]
["","","","Hoog","kW","8.82"]
["Opgenomen vermogen","Laag","","","kW","0.02"]
["","Hoog","","","kW","0.069"]
["Afmetingen","Unit","","Hoogte","mm","287"]
["","","","Breedte","mm","837"]
["","","","Diepte","mm","921"]
["Gewicht","Unit","","","kg","27"]
["Ventilator-","Luchthoeveelheid","","Laag","m³/u","686"]
["","","","Hoog","m³/u","1,296"]
["Totaal geluidsniveau","Laag","","","dB(A)","36"]
["","Hoog","","","dB(A)","52"]
["Geluidsdrukniveau op 1 m","Geluidsdrukniveau op 1 m-=-Laag-=-dBA","","","dB(A)","23"]
["","Geluidsdrukniveau op 1 m-=-Hoog-=-dBA","","","dB(A)","39"]
["Waterdebiet","Koeling","","Laag","l/u","776"]
["","","","Hoog","l/u","1,295"]
["","Verwarming","","Laag","l/u","459"]
["","","","Hoog","l/u","759"]
["","Waterdrukverlies","Koeling","Laag","kPa","13"]
["","","","Hoog","kPa","25"]
["","","Verwarming","Laag","kPa","13"]
["","","","Hoog","kPa","24"]
["Ledingaansluitingen","Water","","Intrede","","3/4\" BSP (vrouwelijke schroefdraad)"]
["Koelleidingmaten","Water","","Uittrede","","3/4\" BSP (vrouwelijke schroefdraad)"]
["","Afvoer","","","mm","VP25 (buitendiam. 32; binnendiam. 25)"]
["Spanningsvorm","Type","","","","230 / 1 / 50"]
["Voeding","Fase","","","","1~"]
["Spanningsvorm","Frequentie","","","Hz","50"]
["","Spanning","","","V","230"]
["Opmerkingen","","","","","(1) - Koelen: lucht 27°CDB, 19°CWB; waterintrede 7℃; wateruittrede 12℃"]
["","","","","","(2) - Verwarming: 2-pijps: 20°C DB, 15°C NB; waterintrede 45°C; waterintrede 40°C;"]
["","","","","","(3) - Verwarming: 4-pijps: 20°C DB, 15°C NB; waterintrede 65°C; waterintrede 55°C;"]
["","","","","","(4) - Voer geen water van minder dan 5°C of meer dan 90°C toe naar de unit, om beschadiging van de unit te voorkomen"]
["","","","","","(5) - Luchtdebiet: 20 °C DB, 15 °C WB 230 V 50 Hz 0 Pa"]