{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":56,"n_cols":11,"rows_kept":56,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXS-F"]
[]
[]
[]
[]
["","","","","","RXS60F4V1B","RXS60F2V1B","RXS60F3V1B","RXS71FAV1B9","RXS71FV1B","RXS71FAV1B"]
["Geluidsdrukniveau op 1 m","Verwarmen","","Hoog","dB(A)","49","","","52"]
["","","","Laag","dB(A)","46","","","49"]
["","Koelen","","Laag","dB(A)","46","","","49"]
["","","","Hoog","dB(A)","49","","","52"]
["Standaard-accessoires","Afvoermof","","","","1","","","1"]
["","Montagehandleiding","","","","1","","","1"]
["Koelmiddel","Charge","","","TCO2Eq","3.1","","","4.8"]
["","GWP","","","","2,087.5","","","2,087.5"]
["","Charge","","","kg","1.5","","","2.3"]
["","Type","","","","R-410A","","","R-410A"]
["Koelleidingmaten","Hoogteverschil","","Max.","m","20","","","20"]
["","Bijkomende koelmiddelvulling","","","kg/m","0,02 (voor leidinglengte van meer dan 10 m)","","","0,02 (voor leidinglengte van meer dan 10 m)"]
["Compressor","Type","","","","Hermetisch gesloten swingcompressor","","","Hermetisch gesloten swingcompressor"]
["Afmetingen","Unit","","Breedte","mm","825","","","900"]
["","","","Diepte","mm","300","","","320"]
["","","","Hoogte","mm","735","","","770"]
["Gewicht","Unit","","","kg","48","","","71"]
["Power supply","Fase","","","","1~","","","1~"]
["","Frequentie","","","Hz","50","","","50"]
["","Spanning","","","V","220-240","","","220-240"]
["Opmerkingen","","","","","(1) - SL: de geluidsarme instelling van de ventilator van de luchtcirculatie","(1) - 220V","","(1) - SL: de geluidsarme instelling van de ventilator van de luchtcirculatie","(1) - 220V"]
["","","","","","(2) - Bevat gefluoreerde broeikasgassen","(2) - 230V","","(2) - Bevat gefluoreerde broeikasgassen","(2) - 230V"]
["Afmetingen","Unit","","Hoogte","mm","","735","735","","770","770"]
["","","","Breedte","mm","","825","825","","900","900"]
["","","","Diepte","mm","","300","300","","320","320"]
["Gewicht","Unit","","","kg","","48","48","","71","71"]
["Compressor","Type","","","","","Hermetisch gesloten swingcompressor","Hermetisch gesloten swingcompressor","","Hermetisch gesloten swingcompressor","Hermetisch gesloten swingcompressor"]
["Werkingsbereik","Koelen","","Min.","°CDB","","-10","-10","","-10","-10"]
["","","","Max.","°CDB","","46","46","","46","46"]
["","Verwarmen","","Min.","°CWB","","-15","-15","","-15","-15"]
["","","","Max.","°CWB","","18","20","","18","20"]
["Geluidsdrukniveau op 1 m","Koelen","","Geluidsdrukniveau op 1 m-=-Koelen-=-Hoog-=-dB(A)","dB(A)","","49","49","","52","52"]
["","","","Geluidsdrukniveau op 1 m-=-Koelen-=-Laag-=-dB(A)","dB(A)","","46","46","","49","49"]
["","Verwarmen","","Geluidsdrukniveau op 1 m-=-Verwarmen-=-Hoog-=-dB(A)","dB(A)","","49","49","","52","52"]
["","","","Geluidsdrukniveau op 1 m-=-Verwarmen-=-Laag-=-dB(A)","dB(A)","","46","46","","49","49"]
["Koelmiddel","Type","","","","","R-410A","R-410A","","R-410A","R-410A"]
["","Vulling","","","kg","","1.5","1.5","","2.3","2.3"]
["Koudemiddel","Vulling","","","tCO2Eq","","3.1","3.1","","4.8","4.8"]
["Koelmiddel","GWP","","","","","2087.5","2087.5","","2087.5","2087.5"]
["Koelleidingmaten","Leidinglengte","","Max.","m","","30","30","","30","30"]
["Leidingaansluitingen","Bijkomende koelmiddelvulling","","","kg/m","","0,02 (voor leidinglengte van meer dan 10 m)","0,02 (voor leidinglengte van meer dan 10 m)","","0,02 (voor leidinglengte van meer dan 10 m)","0,02 (voor leidinglengte van meer dan 10 m)"]
["Koelleidingmaten","Hoogteverschil","","Max.","m","","20","20","","20","20"]
["Standaard-accessoires","Installation manual","","","","","Installation manual","1","","Installation manual","1"]
["","Drain plug","","","","","Drain plug","","","Drain plug"]
["Voeding","Fase","","","","","1~","1~","","1~","1~"]
["Spanningsvorm","Frequentie","","","Hz","","50","50","","50","50"]
["","Spanning","","","V","","220-240","220-240","","220-240","220-240"]
["Opmerkingen","","","","","","(3) - 240V","","","(3) - 240V"]
["Standaard-accessoires","Drain socket","","","","","","1","","","1"]
["Sound power level","Koelen","","","dB(A)","","","","65"]