{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":65,"n_cols":8,"rows_kept":65,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","4MXS-F"]
[]
[]
[]
[]
["","","","","","4MXS68F3V1B2","4MXS68F3V1B","4MXS68F2V1B"]
["Geluidsdrukniveau op 1 m","Verwarmen","","Nom.","dB(A)","49","49"]
["","Koelen","","Nom.","dB(A)","48","48"]
["Standaard-accessoires","Montagehandleiding","","","","1","1"]
["","Aftapplug","","","","1","1"]
["","Montage verloopstuk","","","","1","1"]
["Koudemiddel","Charge","","","TCO2Eq","5.4","5.4"]
["","GWP","","","","2,087.5","2,087.5"]
["","Vulling","","","kg","2.6","2.6"]
["","Type","","","","R-410A","R-410A"]
["Werkingsbereik","Koelen","","Max.","°CDB","46"]
["","","","Min.","°CDB","-10"]
["","Verwarmen","Max.","Max.","°CWB","18"]
["","","","Min.","°CWB","-15"]
["Koelleidingmaten","Hoogteverschil","IU - IU","Max.","m","7.5"]
["","","","Max.","m","15"]
["","Bijkomende koelmiddelvulling","","","kg/m","0,02 (voor leidinglengte van meer dan 30 m)"]
["","Totale leidinglengte","Systeem","Werkelijk","m","60"]
["Compressor","Type","","","","Hermetisch gesloten swingcompressor"]
["Afmetingen","Unit","","Breedte","mm","936","936"]
["","","","Diepte","mm","300","300"]
["","","","Hoogte","mm","735","735"]
["Gewicht","Unit","","","kg","58","58"]
["Power supply","Phase","","","","1~","1~"]
["","Frequentie","","","Hz","50","50"]
["","Spanning","","","V","230","230"]
["Opmerkingen","","","","","(1) - Koelen: binnentemp. 27°CDB, 19,0°CNB, buitentemp. 35°CDB; equivalente leidinglengte: 5m","(1) - Koelen: binnentemp. 27°CDB, 19,0°CNB, buitentemp. 35°CDB; equivalente leidinglengte: 5m"]
["","","","","","(2) - Verwarmen: binnentemp. 20°CDB; buitentemp. 7°CDB/6°CWB; equivalente koelmiddelleidinglengte: 5m","(2) - Verwarmen: binnentemp. 20°CDB; buitentemp. 7°CDB/6°CWB; equivalente koelmiddelleidinglengte: 5m"]
["","","","","","(3) - Bevat gefluoreerde broeikasgassen","(3) - Bevat gefluoreerde broeikasgassen"]
["Koelleidingmaten","Hoogteverschil","IU - IU","Max.","m","","7.5"]
["","","","Max.","m","","15"]
["","Bijkomende koelmiddelvulling","","","kg/m","","0,02 (voor leidinglengte van meer dan 30 m)"]
["","Totale leidinglengte","Systeem","Werkelijk","m","","60"]
["Compressor","Type","","","","","Hermetisch gesloten swingcompressor"]
["Afmetingen","Unit","","Hoogte","mm","","","735"]
["","","","Breedte","mm","","","936"]
["","","","Diepte","mm","","","300"]
["Gewicht","Unit","","","kg","","","58"]
["Compressor","Type","","","","","","Hermetisch gesloten swingcompressor"]
["Werkingsbereik","Koelen","","Min.","°CDB","","","-10"]
["","","","Max.","°CDB","","","46"]
["","Verwarmen","","Min.","°CWB","","","-15"]
["","","","Max.","°CWB","","","15.5"]
["Geluidsdrukniveau op 1 m","Koelen","","Nom.","dB(A)","","","48"]
["","Verwarmen","","Nom.","dB(A)","","","49"]
["Koelmiddel","Type","","","","","","R-410A"]
["","Vulling","","","kg","","","2.6"]
["Koudemiddel","Vulling","","","tCO2Eq","","","5.4"]
["Koelmiddel","GWP","","","","","","2087.5"]
["Koelleidingmaten","Leidinglengte","","Max.","m","","","25"]
["Leidingaansluitingen","Bijkomende koelmiddelvulling","","","kg/m","","","0,02 (voor leidinglengte van meer dan 30 m)"]
["Koelleidingmaten","Hoogteverschil","","Max.","m","","","15"]
["","","IU - IU","Max.","m","","","7.5"]
["","Totale leidinglengte","Systeem","Werkelijk","m","","","60"]
["Standaard-accessoires","Installation manual","","","","","","1"]
["","Drain plug","","","","","","1"]
["","Reducer assembly","","","","","","1"]
["Voeding","Fase","","","","","","1~"]
["Spanningsvorm","Frequentie","","","Hz","","","50"]
["","Spanning","","","V","","","230"]