{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":69,"n_cols":8,"rows_kept":69,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXM-ATV3R"]
[]
[]
[]
[]
["","","","","","FWXM10AATV3R","FWXM15AATV3R","FWXM20AATV3R"]
["Koelvermogen","7/12°C","","Min.","kW","0.75","1.15","1.32"]
["","","","Med.","kW","1.36","2.08","2.39"]
["","","","Max.","kW","2.12","2.81","3.30"]
["Voelbaar koelvermogen","7/12°C","","Min.","kW","0.59","0.83","1.02"]
["","","","Med.","kW","1.04","1.51","1.84"]
["","","","Max.","kW","1.54","2.11","2.65"]
["Verwarmingscapaciteit","45/40°C","","Min.","kW","0.82","1.20","1.47"]
["","","","Med.","kW","1.53","2.16","2.59"]
["","","","Max.","kW","2.21","3.02","3.81"]
["Opgenomen vermogen","Min.","","","kW","0","0.01","0.01"]
["","Med.","","","kW","0.01","0.01","0.01"]
["","Max.","","","kW","0.02","0.02","0.03"]
["Ventilatorsnelheid","Min.","","","rpm","680.00","680.00","680.00"]
["","Med.","","","rpm","1100.00","1100.00","1100.00"]
["","Max.","","","rpm","1500.00","1500.00","1500.00"]
["Behuizing","Kleur","","","","ingebouwd","ingebouwd","ingebouwd"]
["","Materiaal","","","","Geen behuizing","Geen behuizing","Geen behuizing"]
["Afmetingen","Unit","","Hoogte","mm","576","576","576"]
["","","","Breedte","mm","725","925","1125"]
["","","","Diepte","mm","126","126","126"]
["","Verpakte unit","","Hoogte","mm","690","690","690"]
["","","","Breedte","mm","830","1030","1230"]
["","","","Diepte","mm","210","210","210"]
["Gewicht","Unit","","","kg","12","15","18"]
["","Verpakte unit","","","kg","13","16","19"]
["Verpakking","Materiaal","","","","Karton","Karton","Karton"]
["","Gewicht","","","kg","1","1","1"]
["Warmtewisselaar","Aantal","","","","1","1","1"]
["","Volume interne spiraal","","","l","0.8","1.13","1.46"]
["","Vullen","","Bedrijfsdruk","bar","10","10","10"]
["Watercircuit","Diameter Koelleidingmaten","","","in","3/4","3/4","3/4"]
["","Leidingsmateriaal","","","","KOPER","KOPER","KOPER"]
["","Druk","Verwarmen","Max.","bar","10","10","10"]
["Watercircuit - afname van de waterdruk","Verwarmen","45/40°C","Min.","kPa","1.50","2.70","3.00"]
["","","","Med.","kPa","4.30","9.30","8.90"]
["","","","Max.","kPa","9.20","19.10","21.20"]
["","Koelen","7/12°C","Min.","kPa","1.90","2.70","2.50"]
["","","","Med.","kPa","4.30","9.90","8.80"]
["","","","Max.","kPa","8.20","17.10","18.00"]
["Watercircuit - waterdebiet","Verwarmen","45/40°C","Min.","kg/u","140.00","210.00","260.00"]
["","","","Med.","kg/u","270.00","380.00","450.00"]
["","","","Max.","kg/u","390.00","530.00","660.00"]
["","Koelen","7/12°C","Min.","kg/u","130.00","200.00","230.00"]
["","","","Med.","kg/u","230.00","360.00","410.00"]
["","","","Max.","kg/u","360.00","480.00","570.00"]
["Geluidsniveau","Min.","","","dB(A)","35","36","36"]
["","Med.","","","dB(A)","45","46","47"]
["","Max.","","","dB(A)","53.0","54.0","55.0"]
["Werkingsbereik","Verwarmen","waterzijdig","Min.","°C","30","30","30"]
["","","","Max.","°C","85","85","85"]
["","Koelen","Waterzijde","Min.","°C","5","5","5"]
["","","","Max.","°C","18","18","18"]
["","Binnenopstelling","Omgeving","Min.","°C DB","0","0","0"]
["","","","Max.","°C DB","45","45","45"]
["Regelsystemen","IR-afstandsbediening","","","","Nee","Nee","Nee"]
["","Geïntegreerd in binnenunit","","","","Ja","Ja","Ja"]
["Voeding","Fase","","","","1~","1~","1~"]
["Spanningsvorm","Frequentie","","","Hz","50","50","50"]
["","Spanning","","","V","230","230","230"]
["Stroomverbruik","Max.","","","W","19","20","29"]
["","Stand-by","","","W","3","4","5"]
["Stroom","Max. bedrijfsstroom","","Verwarmen","A","0.16","0.18","0.26"]
["","","","Koelen","A","0.16","0.18","0.26"]