{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":77,"n_cols":11,"rows_kept":77,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXT-ATV3CL"]
[]
[]
[]
[]
["","","","","","FWXT10ABTV3CL","FWXT15ABTV3CL","FWXT20ABTV3CL","FWXT10AATV3CL (Archived)","FWXT15AATV3CL (Archived)","FWXT20AATV3CL (Archived)"]
["Afmetingen","Unit","","Breedte","mm","","","","902","1,100","1,300"]
["","","","Diepte","mm","","","","128","128","128"]
["","","","Hoogte","mm","","","","335","335","335"]
["Behuizing","Kleur","","","","","","","RAL 9003","RAL 9003","RAL 9003"]
["Gewicht","Unit","","","kg","","","","14.0","16.0","19.0"]
["Power supply","Fase","","","","","","","1~","1~","1~"]
["","Frequentie","","","Hz","","","","50","50","50"]
["","Spanning","","","V","","","","230","230","230"]
["Koelvermogen","7/12°C","","Min.","kW","0.49","0.62","0.70"]
["","","","Med.","kW","0.88","1.08","1.21"]
["","","","Max.","kW","1.24","1.61","1.94"]
["Voelbaar koelvermogen","7/12°C","","Min.","kW","0.37","0.52","0.57"]
["","","","Med.","kW","0.70","0.86","1.02"]
["","","","Max.","kW","0.98","1.27","1.52"]
["Verwarmingscapaciteit","45/40°C","","Min.","kW","0.55","0.79","0.74"]
["","","","Med.","kW","1.00","1.36","1.55"]
["","","","Max.","kW","1.50","2.01","2.13"]
["Opgenomen vermogen","Min.","","","kW","0.01","0.01","0.01"]
["","Med.","","","kW","0.01","0.01","0.01"]
["","Max.","","","kW","0.02","0.02","0.03"]
["Ventilatorsnelheid","Min.","","","tpm","680.00","680.00","680.00"]
["","Med.","","","tpm","1100.00","1100.00","1100.00"]
["","Max.","","","tpm","1500.00","1500.00","1500.00"]
["Behuizing","Kleur","","","","RAL 9003","RAL 9003","RAL 9003"]
["","Materiaal","","","","Metaalplaat","Metaalplaat","Metaalplaat"]
["Afmetingen","Unit","","Hoogte","mm","335","335","335"]
["","","","Breedte","mm","902","1102","1302"]
["","","","Diepte","mm","128","128","128"]
["","Verpakte unit","","Hoogte","mm","490","490","490"]
["","","","Breedte","mm","1030","1230","1430"]
["","","","Diepte","mm","210","210","210"]
["Gewicht","Unit","","","kg","14","16","19"]
["","Verpakte unit","","","kg","15","17","20"]
["Verpakking","Materiaal","","","","Karton","Karton","Karton"]
["","Gewicht","","","kg","1","1","1"]
["Warmtewisselaar","Aantal","","","","1","1","1"]
["","Volume interne spiraal","","","l","0.5","0.61","0.77"]
["","Vullen","","Bedrijfsdruk","bar","10","10","10"]
["Watercircuit","Diameter Koelleidingmaten","","","in","3/4","3/4","3/4"]
["","Leidingsmateriaal","","","","KOPER","KOPER","KOPER"]
["","Druk","Verwarmen","Max.","bar","10","10","10"]
["Watercircuit - afname van de waterdruk","Verwarmen","45/40°C","Min.","kPa","5.10","4.81","6.00"]
["","","","Med.","kPa","12.00","6.30","6.40"]
["","","","Max.","kPa","16.30","7.20","8.10"]
["","Koelen","7/12°C","Min.","kPa","4.80","4.70","5.50"]
["","","","Med.","kPa","10.50","5.60","5.40"]
["","","","Max.","kPa","11.70","5.10","5.30"]
["Watercircuit - waterdebiet","Verwarmen","45/40°C","Min.","kg/u","100.00","140","150.00"]
["","","","Med.","kg/u","170.00","240","300.00"]
["","","","Max.","kg/u","260.00","350","420.00"]
["","Koelen","7/12°C","Min.","kg/u","80.00","110","120.00"]
["","","","Med.","kg/u","150.00","190","210.00"]
["","","","Max.","kg/u","210.00","280","330.00"]
["Geluidsniveau","Min.","","","dB(A)","35","36","37"]
["","Med.","","","dB(A)","46","47","48"]
["","Max.","","","dB(A)","53.0","54.0","55.0"]
["Werkingsbereik","Verwarmen","waterzijdig","Min.","°C","30","30","30"]
["","","","Max.","°C","85","85","85"]
["","Koelen","Waterzijde","Min.","°C","5","5","5"]
["","","","Max.","°C","18","18","18"]
["","Binnenopstelling","Omgeving","Min.","°CDB","0","0","0"]
["","","","Max.","°CDB","45","45","45"]
["Regelsystemen","IR-afstandsbediening","","","","Voor FWXT-ATV3(C)(CL)","Voor FWXT-ATV3(C)(CL)","Voor FWXT-ATV3(C)(CL)"]
["","Geïntegreerd in binnenunit","","","","Ja","Ja","Ja"]
["Voeding","Fase","","","","1~","1~","1~"]
["Spanningsvorm","Frequentie","","","Hz","50","50","50"]
["","Spanning","","","V","230","230","230"]
["Stroomverbruik","Max.","","","W","19","20","29"]
["","Stand-by","","","W","3","4","5"]
["Stroom","Max. bedrijfsstroom","","Verwarmen","A","0.16","0.18","0.24"]
["","","","Koelen","A","0.16","0.18","0.24"]