{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":73,"n_cols":11,"rows_kept":73,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXT-ATV3CL"]
[]
[]
[]
[]
["","","","","","FWXT10ABTV3CL","FWXT10AATV3CL","FWXT15ABTV3CL","FWXT15AATV3CL","FWXT20ABTV3CL","FWXT20AATV3CL"]
["Koelvermogen","7/12°C","","Min.","kW","0.49","0.48","0.62","0.58","0.70","0.91"]
["","","","Med.","kW","0.88","0.80","1.08","1.03","1.21","1.75"]
["","","","Max.","kW","1.24","1.07","1.61","1.65","1.94","2.31"]
["Voelbaar koelvermogen","7/12°C","","Min.","kW","0.37","0.39","0.52","0.49","0.57","0.76"]
["","","","Med.","kW","0.70","0.69","0.86","0.91","1.02","1.53"]
["","","","Max.","kW","0.98","0.95","1.27","1.49","1.52","1.94"]
["Verwarmingscapaciteit","45/40°C","","Min.","kW","0.55","0.53","0.79","0.66","0.74","0.96"]
["","","","Med.","kW","1.00","0.94","1.36","1.26","1.55","1.98"]
["","","","Max.","kW","1.50","1.27","2.01","1.80","2.13","2.60"]
["Opgenomen vermogen","Min.","","","kW","0.01","0","0.01","0.01","0.01","0.01"]
["","Med.","","","kW","0.01","","0.01","","0.01"]
["","Max.","","","kW","0.02","0.01","0.02","0.01","0.03","0.02"]
["Ventilatorsnelheid","Min.","","","rpm","680.00","","680.00","","680.00"]
["","Med.","","","rpm","1100.00","","1100.00","","1100.00"]
["","Max.","","","rpm","1500.00","","1500.00","","1500.00"]
["Behuizing","Kleur","","","","RAL 9003","RAL 9003","RAL 9003","RAL 9003","RAL 9003","RAL 9003"]
["","Materiaal","","","","Metaalplaat","Metaalplaat","Metaalplaat","Metaalplaat","Metaalplaat","Metaalplaat"]
["Afmetingen","Unit","","Hoogte","mm","335","335","335","335","335","335"]
["","","","Breedte","mm","902","902","1102","1100","1302","1300"]
["","","","Diepte","mm","128","128","128","128","128","128"]
["","Verpakte unit","","Hoogte","mm","490","490","490","490","490","490"]
["","","","Breedte","mm","1030","1030","1230","1230","1430","1430"]
["","","","Diepte","mm","210","210","210","210","210","210"]
["Gewicht","Unit","","","kg","14","14","16","16","19","19"]
["","Verpakte unit","","","kg","15","15","17","17","20","20"]
["Verpakking","Materiaal","","","","Karton","Karton","Karton","Karton","Karton","Karton"]
["","Gewicht","","","kg","1","1","1","1","1","1"]
["Warmtewisselaar","Aantal","","","","1","1","1","1","1","1"]
["","Volume interne spiraal","","","l","0.5","0.5","0.61","0.7","0.77","0.9"]
["","Vullen","","Bedrijfsdruk","bar","10","10","10","10","10","10"]
["Watercircuit","Diameter Koelleidingmaten","","","in","3/4","3/4","3/4","3/4","3/4","3/4"]
["","Leidingsmateriaal","","","","KOPER","Koper (CW617N)","KOPER","Koper (CW617N)","KOPER","Koper (CW617N)"]
["","Druk","Verwarmen","Max.","bar","10","10","10","10","10","10"]
["Watercircuit - afname van de waterdruk","Verwarmen","45/40°C","Min.","kPa","5.10","1.10","4.81","2.80","6.00","1.10"]
["","","","Med.","kPa","12.00","3.10","6.30","3.50","6.40","4.10"]
["","","","Max.","kPa","16.30","5.40","7.20","4.00","8.10","6.60"]
["","Koelen","7/12°C","Min.","kPa","4.80","1.10","4.70","3.90","5.50","1.30"]
["","","","Med.","kPa","10.50","3.00","5.60","4.80","5.40","4.20"]
["","","","Max.","kPa","11.70","5.20","5.10","5.70","5.30","6.90"]
["Watercircuit - waterdebiet","Verwarmen","45/40°C","Min.","kg/u","100.00","91.90","140","112.60","150.00","164.80"]
["","","","Med.","kg/u","170.00","162.00","240","216.60","300.00","341.00"]
["","","","Max.","kg/u","260.00","218.40","350","310.00","420.00","447.20"]
["","Koelen","7/12°C","Min.","kg/u","80.00","82.10","110","98.90","120.00","156.50"]
["","","","Med.","kg/u","150.00","138.10","190","177.40","210.00","300.60"]
["","","","Max.","kg/u","210.00","184.40","280","283.00","330.00","396.80"]
["Geluidsniveau","Min.","","","dB(A)","35","34","36","34","37","35"]
["","Med.","","","dB(A)","46","","47","","48"]
["","Max.","","","dB(A)","53.0","","54.0","","55.0"]
["Werkingsbereik","Verwarmen","waterzijdig","Min.","°C","30","30","30","30","30","30"]
["","","","Max.","°C","85","85","85","85","85","85"]
["","Koelen","Waterzijde","Min.","°C","5","5","5","5","5","5"]
["","","","Max.","°C","18","18","18","18","18","18"]
["","Binnenopstelling","Omgeving","Min.","°C DB","0","0","0","0","0","0"]
["","","","Max.","°C DB","45","45","45","45","45","45"]
["Regelsystemen","IR-afstandsbediening","","","","Voor FWXT-ATV3(C)(CL)","","Voor FWXT-ATV3(C)(CL)","","Voor FWXT-ATV3(C)(CL)"]
["","Geïntegreerd in binnenunit","","","","Ja","Nee","Ja","Nee","Ja","Nee"]
["Voeding","Fase","","","","1~","1~","1~","1~","1~","1~"]
["Spanningsvorm","Frequentie","","","Hz","50","50","50","50","50","50"]
["","Spanning","","","V","230","230","230","230","230","230"]
["Stroomverbruik","Max.","","","W","19","18","20","20","29","27"]
["","Stand-by","","","W","3","5","4","5","5","6"]
["Stroom","Max. bedrijfsstroom","","Verwarmen","A","0.16","0.2","0.18","0.2","0.24","0.2"]
["","","","Koelen","A","0.16","0.2","0.18","0.2","0.24","0.2"]
["Ventilatorsnelheid","Ventilatorsnelheid-=-Min.-=-rpm","","","rpm","","84.00","","124.00","","138.00"]
["","Ventilatorsnelheid-=-Med.-=-rpm","","","rpm","","155.00","","229.00","","283.00"]
["","Ventilatorsnelheid-=-Max.-=-rpm","","","rpm","","228.00","","331.00","","440.00"]
["Geluidsniveau","Geluidsniveau-=-Max.-=-dBA","","","dB(A)","","49.0","","51.0","","52.0"]