{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":73,"n_cols":11,"rows_kept":73,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXV-ATV3R"]
[]
[]
[]
[]
["","","","","","FWXV10ABTV3R","FWXV10AATV3R","FWXV15ABTV3R","FWXV15AATV3R","FWXV20ABTV3R","FWXV20AATV3R"]
["Koelvermogen","7/12°C","","Min.","kW","0.78","0.66","1.10","1.30","1.13","1.82"]
["","","","Med.","kW","1.11","1.36","1.65","2.16","1.98","2.52"]
["","","","Max.","kW","1.62","1.77","2.64","2.89","2.99","3.20"]
["Voelbaar koelvermogen","7/12°C","","Min.","kW","0.58","0.39","0.82","0.99","0.85","1.22"]
["","","","Med.","kW","0.71","0.98","1.15","1.53","1.55","1.55"]
["","","","Max.","kW","1.25","1.33","1.91","2.10","2.33","1.78"]
["Verwarmingscapaciteit","45/40°C","","Min.","kW","0.87","0.95","1.12","1.24","1.11","1.90"]
["","","","Med.","kW","1.27","1.63","1.83","2.33","2.32","3.05"]
["","","","Max.","kW","1.96","2.18","2.86","3.11","3.50","3.88"]
["Opgenomen vermogen","Min.","","","kW","0.01","0","0.01","0","0.01","0.01"]
["","Med.","","","kW","0.01","","0.01","","0.01"]
["","Max.","","","kW","0.02","0.02","0.03","0.02","0.03","0.03"]
["Ventilatorsnelheid","Min.","","","tpm","720.00","","720.00","","720.00"]
["","Med.","","","tpm","1220.00","","1220.00","","1220.00"]
["","Max.","","","tpm","1700.00","","1700.00","","1700.00"]
["Behuizing","Kleur","","","","RAL 9003","RAL 9003","RAL 9003","RAL 9003","RAL 9003","RAL 9003"]
["","Materiaal","","","","Metaalplaat","Metaalplaat","Metaalplaat","Metaalplaat","Metaalplaat","Metaalplaat"]
["Afmetingen","Unit","","Hoogte","mm","601","601","601","601","601","601"]
["","","","Breedte","mm","999","999","1199","1200","1399","1400"]
["","","","Diepte","mm","135","135","135","135","135","135"]
["","Verpakte unit","","Hoogte","mm","690","690","690","690","690","690"]
["","","","Breedte","mm","1230","1230","1430","1430","1630","1630"]
["","","","Diepte","mm","210","210","210","210","210","210"]
["Gewicht","Unit","","","kg","20","20","23","23","26","26"]
["","Verpakte unit","","","kg","21","21","24","24","27","27"]
["Verpakking","Materiaal","","","","Karton","Karton","Karton","Karton","Karton","Karton"]
["","Gewicht","","","kg","1","1","1","1","1","1"]
["Warmtewisselaar","Aantal","","","","1","1","1","1","1","1"]
["","Volume interne spiraal","","","l","0.8","0.8","1.1","1.1","1.5","1.5"]
["","Vullen","","Bedrijfsdruk","bar","10","10","10","10","10","10"]
["Watercircuit","Diameter Koelleidingmaten","","","in","3/4","3/4","3/4","3/4","3/4","3/4"]
["","Leidingsmateriaal","","","","KOPER","Koper (CW617N)","KOPER","Koper (CW617N)","KOPER","Koper (CW617N)"]
["","Druk","Verwarmen","Max.","bar","10","10","10","10","10","10"]
["Watercircuit - afname van de waterdruk","Verwarmen","45/40°C","Min.","kPa","7.00","1.30","9.00","8.60","8.00","3.80"]
["","","","Med.","kPa","8.00","4.20","14.00","3.30","15.00","11.20"]
["","","","Max.","kPa","11.00","7.20","23.00","11.50","22.00","21.30"]
["","Koelen","7/12°C","Min.","kPa","7.00","1.20","9.00","4.30","8.00","2.10"]
["","","","Med.","kPa","8.00","2.80","14.00","19.30","15.00","13.10"]
["","","","Max.","kPa","11.00","2.90","23.00","27.00","22.00","24.00"]
["Watercircuit - waterdebiet","Verwarmen","45/40°C","Min.","kg/u","150.00","163.50","200.00","212.50","190.00","327.00"]
["","","","Med.","kg/u","220.00","280.30","320.00","401.10","400.00","524.60"]
["","","","Max.","kg/u","340.00","374.10","500.00","534.50","610.00","667.50"]
["","Koelen","7/12°C","Min.","kg/u","130.00","113.50","190.00","223.70","190.00","313.00"]
["","","","Med.","kg/u","190.00","234.10","280.00","371.70","340.00","433.60"]
["","","","Max.","kg/u","280.00","303.60","450.00","496.60","510.00","550.60"]
["Geluidsniveau","Min.","","","dB(A)","40","34","42","35","43","35"]
["","Med.","","","dB(A)","47","43","49","43","50","44"]
["","Max.","","","dB(A)","56.0","","57.0","","58.0"]
["Werkingsbereik","Verwarmen","waterzijdig","Min.","°C","30","30","30","30","30","30"]
["","","","Max.","°C","85","85","85","85","85","85"]
["","Koelen","Waterzijde","Min.","°C","5","5","5","5","5","5"]
["","","","Max.","°C","18","18","18","18","18","18"]
["","Binnenopstelling","Omgeving","Min.","°CDB","0","0","0","0","0","0"]
["","","","Max.","°CDB","45","45","45","45","45","45"]
["Regelsystemen","IR-afstandsbediening","","","","Nee","Nee","Nee","Nee","Nee","Nee"]
["","Geïntegreerd in binnenunit","","","","Ja","Ja","Ja","Ja","Ja","Ja"]
["Voeding","Fase","","","","1~","1~","1~","1~","1~","1~"]
["Spanningsvorm","Frequentie","","","Hz","50","50","50","50","50","50"]
["","Spanning","","","V","230","230","230","230","230","230"]
["Stroomverbruik","Max.","","","W","19","19","25","20","31","29"]
["","Stand-by","","","W","3","3","4","4","5","5"]
["Stroom","Max. bedrijfsstroom","","Verwarmen","A","0.15","0.2","0.21","0.2","0.27","0.3"]
["","","","Koelen","A","0.15","0.2","0.21","0.2","0.27","0.3"]
["Ventilatorsnelheid","Ventilatorsnelheid-=-Min.-=-rpm","","","tpm","","118.00","","180.00","","246.00"]
["","Ventilatorsnelheid-=-Med.-=-rpm","","","tpm","","210.00","","318.00","","410.00"]
["","Ventilatorsnelheid-=-Max.-=-rpm","","","tpm","","294.00","","438.00","","566.00"]
["Geluidsniveau","Geluidsniveau-=-Max.-=-dBA","","","dB(A)","","51.0","","53.0","","55.0"]