{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":77,"n_cols":14,"rows_kept":77,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","LREQ-BY1"]
[]
[]
[]
[]
["","","","","","LREQ5B7Y1","LREQ6B7Y1","LREQ8B7Y1","LREQ10B7Y1","LREQ12B7Y1","LREQ15B7Y1","LREQ20B7Y1","LREQ30B7Y1","LREQ40B7Y1"]
["Koelvermogen","Lage temperatuur","","kW","kW","5.51 (2)","6.51 (2)","8.33 (2)","10.0 (2)","10.7 (2)","13.9 (2)","15.4 (2)","27.8","29.6"]
["","Middelhoge temperatuur","","kW","kW","12.5 (1)","15.2 (1)","19.8 (1)","23.8 (1)","26.5 (1)","33.9 (1)","37.9 (1)","67.8 (3)","75.8 (3)"]
["Opgenomen vermogen","Lage temperatuur","","Nom.","kW","4.65 (2)","5.88 (2)","7.72 (2)","9.27 (2)","9.89 (2)","12.8 (2)","14.1 (2)","25.6","27.6"]
["","Middelhoge temperatuur","","Nom.","kW","5.1","6.56 (1)","8.76 (1)","10.6 (1)","12.0 (1)","15.2 (1)","17.0 (1)","30.4","34.0"]
["Werkingsbereik","Omgevingstemperatuur","","Min.","°C","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°C","43","43","43","43","43","43","43"]
["","Verdamper","Koelen","Min.","°C DB","-45","-45","-45","-45","-45","-45","-45"]
["","","","Max.","°C DB","10","10","10","10","10","10","10"]
["Jaarlijks elektriciteitsverbruik Q","R-410A","","Te -10°C","kWu/a","19907","24681","33483","42794","46377","61683","72030"]
["","","","Te -35°C","kWu/a","22805","27453","33817","39747","44363","61090","67325"]
["SEPR (seizoensgebaseerde energieprestatie-ratio)","R-410A","","Te -10°C","","3.86","3.79","3.64","3.42","3.51","3.38","3.23"]
["","","","Te -35°C","","1.80","1.77","1.84","1.88","1.80","1.70","1.70"]
["Parameters bij vollast en omgevingstemp. 32°C (punt A)","R-410A","Te -10°C","Nom. koelvermogen (PA)","kW","12.50","15.20","19.80","23.80","26.50","33.90","37.90"]
["","","","Nom. opgenomen vermogen (DA)","kW","5.10","6.56","8.76","10.60","12.00","15.20","17.00"]
["","","","Nom. COP (COPA)","","2.45","2.32","2.26","2.25","2.21","2.23","2.23"]
["","","Te -35°C","Nom. koelvermogen (PA)","kW","5.51","6.51","8.33","10.00","10.70","13.90","15.40"]
["","","","Nom. opgenomen vermogen (DA)","kW","4.65","5.88","7.72","9.27","9.89","12.80","14.10"]
["","","","Nom. COP (COPA)","","1.18","1.11","1.08","1.08","1.08","1.09","1.09"]
["Parameters bij vollast en omgevingstemp. 43°C","R-410A","Te -10°C","Vermelde COP (COP3)","","1.54","1.57","1.40","1.46","1.47","1.46","1.51"]
["","","Te -35°C","Vermelde COP (COP3)","","0.76","0.74","0.68","0.70","0.71","0.71","0.74"]
["Compressor 2","Type","","","","","","Hermetisch gesloten scrollcompressor","Hermetisch gesloten scrollcompressor","Hermetisch gesloten scrollcompressor","Hermetisch gesloten scrollcompressor","Hermetisch gesloten scrollcompressor"]
["Ventilatormotor","Aandrijving","","","","Directe aandrijving","Directe aandrijving","Directe aandrijving","Directe aandrijving","Directe aandrijving","Directe aandrijving","Directe aandrijving"]
["Ventilatormotor 2","Output","","","W","","","","","","350","750"]
["Ventilator","Aantal","","","","1","1","1","1","1","2","2"]
["","Type","","","","Schroefventilator","Schroefventilator","Schroefventilator","Schroefventilator","Schroefventilator","Schroefventilator","Schroefventilator"]
["Ventilator-","Luchthoeveelheid","Koelen","Nom.","m³/min","95","102","171","179","191","230","240"]
["Ventilatormotor","Output","","","W","350","350","750","750","750","350","750"]
["Koelleidingmaten","Vloeistof","","50 m of minder","","ø 9,5 C1220T (hardsoldeerverbinding)","ø 9,5 C1220T (hardsoldeerverbinding)","ø 9,5 C1220T (hardsoldeerverbinding)","ø 9,5 C1220T (hardsoldeerverbinding)","ø 12,7 C1220T (hardsoldeerverbinding)","ø 12,7 C1220T (hardsoldeerverbinding)","ø 12,7 C1220T (hardsoldeerverbinding)","ø 19,05 C1220T (hardsoldeerverbinding)","ø 19,05 C1220T (hardsoldeerverbinding)"]
["","","","50~130 m","","Ø 9.5 C1220T (Brazing connection)","Ø 9.5 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","ø 19.05 C1220T (Brazing connection)","ø 19.05 C1220T (Brazing connection)"]
["","Gas","","50 m of minder","","ø 22,2 C1220T (hardsoldeerverbinding)","ø 22,2 C1220T (hardsoldeerverbinding)","ø 28,6 C1220T (hardsoldeerverbinding)","ø 28,6 C1220T (hardsoldeerverbinding)","ø 28,6 C1220T (hardsoldeerverbinding)","ø 34,9 C1220T (hardsoldeerverbinding)","ø 34,9 C1220T (hardsoldeerverbinding)","ø 41,28 C1220T (hardsoldeerverbinding)","ø 41,28 C1220T (hardsoldeerverbinding)"]
["","","","50~130 m","","ø 22.2 C1220T (Brazing connection)","ø 22.2 C1220T (Brazing connection)","Ø 28.6 C1220T (Brazing connection)","Ø 28.6 C1220T (Brazing connection)","Ø 28.6 C1220T (Brazing connection)","ø 34.9 C1220T (Brazing connection)","ø 34.9 C1220T (Brazing connection)","ø 41.28 C1220T (Brazing connection)","ø 41.28 C1220T (Brazing connection)"]
["Afmetingen","Unit","","Hoogte","mm","1680","1680","1680","1680","1680","1680","1680"]
["","","","Breedte","mm","635","635","930","930","930","1240","1240"]
["","","","Diepte","mm","765","765","765","765","765","765","765"]
["Gewicht","Unit","","","kg","166","166","242","242","242","331","337"]
["Koelmiddel","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Behuizing","Kleur","","","","Ivoorwit (Munsell code: 5Y7.5/1)","Ivoorwit (Munsell code: 5Y7.5/1)","Ivoorwit (Munsell code: 5Y7.5/1)","Ivoorwit (Munsell code: 5Y7.5/1)","Ivoorwit (Munsell code: 5Y7.5/1)","Ivoorwit (Munsell code: 5Y7.5/1)","Ivoorwit (Munsell code: 5Y7.5/1)"]
["Koelmiddel","GWP","","","","2087.5","2087.5","2087.5","2087.5","2087.5","2087.5","2087.5"]
["Warmtewisselaar","Type","","","","Kruiselings geribd blok","Kruiselings geribd blok","Kruiselings geribd blok","Kruiselings geribd blok","Kruiselings geribd blok","Kruiselings geribd blok","Kruiselings geribd blok"]
["Koelmiddel","Vulling","","","kg","5.2","5.2","7.9","7.9","7.9","11.5","11.5"]
["Koudemiddel","Vulling","","","tCO2Eq","10.9","10.9","16.5","16.5","16.5","24.0","24.0"]
["Standaard-accessoires","Installation manual","","","","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual"]
["","Clamping materials","","","","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials"]
["","Refrigerant label for F-gas regulation","","","","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation"]
["","Operation manual","","","","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual"]
["","Connection pipes","","","","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes"]
["","Additional refrigerant label","","","","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label"]
["Voeding","Fase","","","","3~","3~","3~","3~","3~","3~","3~"]
["Spanningsvorm","Frequentie","","","Hz","50","50","50","50","50","50","50"]
["","Spanning","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Stroom","Nominale bedrijfsstroom - 50Hz","Compressor 2","Koelen","A","","","7.5","7.9","8.3","8.2","8.4"]
["","","Compressor 1","Koelen","A","7.1","9.2","5.3","7.4","9.8","7.0","9.5"]
["","","Compressor 3","Koelen","A","","","","","","8.2","8.4"]
["Opmerkingen","","","","","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Wanneer de doelverdampingstemperatuur -20°C of lager is, kan koelmiddelolie worden toegevoegd. Als koelmiddelolie wordt toegevoegd, kan de doelverdampingstemperatuur niet stijgen tot -20°C of hoger.","(1) - Wanneer de doelverdampingstemperatuur -20°C of lager is, kan koelmiddelolie worden toegevoegd. Als koelmiddelolie wordt toegevoegd, kan de doelverdampingstemperatuur niet stijgen tot -20°C of hoger."]
["","","","","","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Bij buitentemperaturen van lager dan -10°C, moet een wind- of sneeuwscherm worden geïnstalleerd. Raadpleeg de onderhoudshandleiding voor meer details.","(2) - Bij buitentemperaturen van lager dan -10°C, moet een wind- of sneeuwscherm worden geïnstalleerd. Raadpleeg de onderhoudshandleiding voor meer details."]
["","","","","","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Sound pressure data: measured at 1m in front of unit, at 1.5m height","(3) - Bedrijfsvoorwaarden voor buitenunit: verdampingstemperatuur = -10°C, buitentemperatuur +32°C, aanzuigzijde SH 10K","(3) - Bedrijfsvoorwaarden voor buitenunit: verdampingstemperatuur = -10°C, buitentemperatuur +32°C, aanzuigzijde SH 10K"]
["","","","","","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - Gebruik de aftakkingskit (EKHRQZM) om een aanzuigleiding tussen de buitenunits te verdelen.","(4) - Gebruik de aftakkingskit (EKHRQZM) om een aanzuigleiding tussen de buitenunits te verdelen."]
["","","","","","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - Gebruik de koelmiddelolie van DAIKIN (blik van 1 liter: onderdeelnr. 5004333)","(5) - Gebruik de koelmiddelolie van DAIKIN (blik van 1 liter: onderdeelnr. 5004333)"]
["","","","","","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - RLA is gebaseerd op de volgende omstandigheden: buitentemperatuur: 32℃; aanzuiging SH 10K; verdampingstemperatuur -10℃;","(6) - RLA is gebaseerd op de volgende omstandigheden: buitentemperatuur: 32℃; aanzuiging SH 10K; verdampingstemperatuur -10℃;"]
["","","","","","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - TOCA means the total value of each OC set.","(7) - TOCA means the total value of each OC set."]
["","","","","","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(8) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Maximum allowable voltage range variation between phases is 2%.","(9) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Compressor 2 and 3","(11) - Compressor 2 and 3"]
["","","","","","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1"]
["","","","","","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2"]
["","","","","","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3","(14) - Compressor 2 and 3"]
["","","","","","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit"]
["","","","","","(16) - Bevat gefluoreerde broeikasgassen","(16) - Bevat gefluoreerde broeikasgassen","(16) - Bevat gefluoreerde broeikasgassen","(16) - Bevat gefluoreerde broeikasgassen","(16) - Bevat gefluoreerde broeikasgassen","(16) - Bevat gefluoreerde broeikasgassen","(16) - Bevat gefluoreerde broeikasgassen"]
["","","","","","(17) - Ecodesign-richtlijn: (EU) 2015/1095","(17) - Ecodesign-richtlijn: (EU) 2015/1095","(17) - Ecodesign-richtlijn: (EU) 2015/1095","(17) - Ecodesign-richtlijn: (EU) 2015/1095","(17) - Ecodesign-richtlijn: (EU) 2015/1095","(17) - Ecodesign-richtlijn: (EU) 2015/1095","(17) - Ecodesign-richtlijn: (EU) 2015/1095"]
["Standaard-accessoires","Ref. oil fill volume label","","","","","","","","","","","Ref. oil fill volume label","Ref. oil fill volume label"]